## Oversikt
Oppetidsrapport – Drivdal
Periode: 2025-01-31 23:00:00+00:00 – 2025-02-28 22:00:00+00:00 UTC
Timer totalt: 672
Data­kvalitet: 672/672 aksepterte, 0 flagget
KPI | Verdi | Enhet | Timer | Confidence | Definisjon
Tidsbaserte KPI-er (IEEE 762 / NERC GADS)
ServiceHours_SH | 370 | hours | 672 | 100% | Antall timer i InService-tilstand
AvailableHours_AH | 421 | hours | 672 | 100% | SH + ReserveShutdownHours (timer verket er tilgjengelig)
UnavailableHours_UH | 230 | hours | 672 | 100% | POH + MOH + FOH (timer verket ikke er tilgjengelig)
ForcedOutageHours_FOH | 163 | hours | 672 | 100% | Timer i ForcedOutage-tilstand
InformationUnavailable_Hours | 0 | hours | 672 | 100% | Timer uten data (ekskluderes fra KPI-nevnere)
ResourceUnavailable_Hours | 0 | hours | 672 | 100% | Timer med ressursbegrensning (OMC)
AvailabilityFactor_AF | 62.65% | ratio | 672 | 77.81% | AF = AH / (PH − OMC − IU). Unit Performance Index.
AvailabilityFactor_AF_SystemView | 62.65% | ratio | 672 | 77.81% | AF inkludert OMC i nevner. System Reliability Index.
ServiceFactor_SF | 55.06% | ratio | 672 | 77.81% | SF = SH / effektive timer
ForcedOutageRate_FOR | 30.58% | ratio | 533 | 77.81% | FOR = FOH / (FOH + SH)
EquivalentForcedDerated_Hours | 10.4538 | hours | 672 | 77.81% | EFDH = Σ (Plan - Elhub) / Pnom for timer i ForcedDerating
EquivalentAvailabilityFactor_EAF | 61.09% | ratio | 672 | 77.81% | EAF = (AH − EFDH) / effektive timer
Energibaserte KPI-er
TotalProduction_MWh | 703.5547 | MWh | 672 | 100% | Σ MWh-Elhub
CapacityFactor_CF | 47.59% | ratio | 672 | 77.81% | CF = Σ Elhub / (Pnom × PH), Pnom=2.2 MW
OutputFactor_OF | 86.43% | ratio | 370 | 77.81% | OF = Σ Elhub / (Pnom × SH)
Hendelsesbaserte KPI-er
ForcedOutageEvents | 22 | events | 672 | 77.81% | Antall sammenhengende ForcedOutage-hendelser
MTBF | 16.8182 | hours | 672 | 77.81% | Mean Time Between Failures = SH / FO-hendelser
MTTR | 7.4091 | hours | 672 | 77.81% | Mean Time To Repair = FOH / FO-hendelser
Plan- og markedsavvik (3-veis sammenligning)
PlanTotal_MWh | 748.582 | MWh | 672 | 100% | Σ Produksjonplan
SpotbudTotal_MWh | 732.2 | MWh | 672 | 100% | Σ Spotbud (Day-Ahead)
PlanFulfillment | 93.98% | ratio | 672 | 100% | Elhub / Plan – andel av planlagt produksjon som ble levert
BidAccuracy | 96.09% | ratio | 672 | 100% | Elhub / Spotbud – andel av markedsforpliktelse som ble levert
PlanToBidDeviation | 2.188% | ratio | 672 | 100% | (Plan − Bud) / Plan – hvor mye av planen ble ikke budt inn
PlanDeviation_MWh | -45.0273 | MWh | 672 | 100% | Elhub − Plan
PlanDeviation_NOK | -52825.6661 | NOK | 672 | 100% | Verdien av planavviket priset til spotpris per time
ImbalanceResult_NOK | 30991.0064 | NOK | 672 | 100% | Tap/gevinst på ubalanse (før gebyrer) – negativ = tap
ImbalanceCorrelation_AbsVol_RKPris | 0.068925 | correlation | 672 | 100% | Korrelasjon mellom ubalansevolum og regulerkraftpris

## Tilstandsfordeling
Tilstandsfordeling per time
UnitState | Timer | Andel
InService | 370 | 55.06%
ForcedOutage | 163 | 24.26%
PlannedOutage | 67 | 9.97%
ReserveShutdown | 51 | 7.589%
ForcedDerating | 21 | 3.125%

## Timer
Time-for-time klassifisering
Time (UTC) | MWh-Elhub | Plan | Spotbud | Spotpris | UnitState | Conf. | Cause | Rationale
2025-01-31 23:00 | 0 | 0 | 0 | 501.21 | ReserveShutdown | 0.55 | M1-MarketDriven | Elhub=0, Plan=0, Spotpris=501 < median 778 – markedsstyrt
2025-02-01 | 0 | 0 | 0 | 499.69 | ReserveShutdown | 0.55 | M1-MarketDriven | Elhub=0, Plan=0, Spotpris=500 < median 778 – markedsstyrt
2025-02-01 01:00 | 0 | 0 | 0 | 498.63 | ReserveShutdown | 0.55 | M1-MarketDriven | Elhub=0, Plan=0, Spotpris=499 < median 778 – markedsstyrt
2025-02-01 02:00 | 0 | 0 | 0 | 495.92 | ReserveShutdown | 0.55 | M1-MarketDriven | Elhub=0, Plan=0, Spotpris=496 < median 778 – markedsstyrt
2025-02-01 03:00 | 0 | 0 | 0 | 503.68 | ReserveShutdown | 0.55 | M1-MarketDriven | Elhub=0, Plan=0, Spotpris=504 < median 778 – markedsstyrt
2025-02-01 04:00 | 0 | 0 | 0 | 520.26 | ReserveShutdown | 0.55 | M1-MarketDriven | Elhub=0, Plan=0, Spotpris=520 < median 778 – markedsstyrt
2025-02-01 05:00 | 0 | 0 | 0 | 537.18 | ReserveShutdown | 0.55 | M1-MarketDriven | Elhub=0, Plan=0, Spotpris=537 < median 778 – markedsstyrt
2025-02-01 06:00 | 0 | 0 | 0 | 651.79 | ReserveShutdown | 0.55 | M1-MarketDriven | Elhub=0, Plan=0, Spotpris=652 < median 778 – markedsstyrt
2025-02-01 07:00 | 1.1284 | 2 | 2 | 895.93 | ForcedDerating | 0.65 | D1-ForcedDerating | Elhub=1.128 = 56% av Plan=2.000 – redusert kapasitet
2025-02-01 08:00 | 2.1937 | 2.1 | 2.2 | 1508.82 | InService | 0.95 | 0-Normal | Elhub=2.194 ≈ Plan=2.100 (ratio=104%)
2025-02-01 09:00 | 2.197 | 2.1 | 2.2 | 1422.3 | InService | 0.95 | 0-Normal | Elhub=2.197 ≈ Plan=2.100 (ratio=105%)
2025-02-01 10:00 | 2.1944 | 2.1 | 2.2 | 1326.5 | InService | 0.95 | 0-Normal | Elhub=2.194 ≈ Plan=2.100 (ratio=104%)
2025-02-01 11:00 | 2.1935 | 2.1 | 2.2 | 1224.83 | InService | 0.95 | 0-Normal | Elhub=2.194 ≈ Plan=2.100 (ratio=104%)
2025-02-01 12:00 | 2.1907 | 2.1 | 2.2 | 1150.07 | InService | 0.95 | 0-Normal | Elhub=2.191 ≈ Plan=2.100 (ratio=104%)
2025-02-01 13:00 | 2.1901 | 2.1 | 2.2 | 1203.67 | InService | 0.95 | 0-Normal | Elhub=2.190 ≈ Plan=2.100 (ratio=104%)
2025-02-01 14:00 | 2.1886 | 2.1 | 2.2 | 1440.29 | InService | 0.95 | 0-Normal | Elhub=2.189 ≈ Plan=2.100 (ratio=104%)
2025-02-01 15:00 | 2.1881 | 2.1 | 2.2 | 1698.77 | InService | 0.95 | 0-Normal | Elhub=2.188 ≈ Plan=2.100 (ratio=104%)
2025-02-01 16:00 | 0.65177 | 0.5 | 2.2 | 1866.74 | InService | 0.95 | 0-Normal | Elhub=0.652 ≈ Plan=0.500 (ratio=130%)
2025-02-01 17:00 | 2.0392 | 2.1 | 2.2 | 1864.39 | InService | 0.95 | 0-Normal | Elhub=2.039 ≈ Plan=2.100 (ratio=97%)
2025-02-01 18:00 | 0.63744 | 0.5 | 2.2 | 1809.73 | InService | 0.95 | 0-Normal | Elhub=0.637 ≈ Plan=0.500 (ratio=127%)
2025-02-01 19:00 | 1.4125 | 1.4 | 1.4 | 1748.73 | InService | 0.95 | 0-Normal | Elhub=1.412 ≈ Plan=1.400 (ratio=101%)
2025-02-01 20:00 | 1.4272 | 1.4 | 1.4 | 1623.54 | InService | 0.95 | 0-Normal | Elhub=1.427 ≈ Plan=1.400 (ratio=102%)
2025-02-01 21:00 | 1.4256 | 1.4 | 1.4 | 986.91 | InService | 0.95 | 0-Normal | Elhub=1.426 ≈ Plan=1.400 (ratio=102%)
2025-02-01 22:00 | 1.4296 | 1.4 | 1.4 | 685.88 | InService | 0.95 | 0-Normal | Elhub=1.430 ≈ Plan=1.400 (ratio=102%)
2025-02-01 23:00 | 0.01792 | 0 | 0 | 612.21 | InService | 0.8 | 0-Normal | Elhub=0.018 (ingen plan-sammenligning)
2025-02-02 | 0 | 0 | 0 | 600.28 | ReserveShutdown | 0.55 | M1-MarketDriven | Elhub=0, Plan=0, Spotpris=600 < median 778 – markedsstyrt
2025-02-02 01:00 | 0 | 0 | 0 | 601.09 | ReserveShutdown | 0.55 | M1-MarketDriven | Elhub=0, Plan=0, Spotpris=601 < median 778 – markedsstyrt
2025-02-02 02:00 | 0 | 0 | 0 | 610.1 | ReserveShutdown | 0.55 | M1-MarketDriven | Elhub=0, Plan=0, Spotpris=610 < median 778 – markedsstyrt
2025-02-02 03:00 | 0 | 0 | 0 | 604.84 | ReserveShutdown | 0.55 | M1-MarketDriven | Elhub=0, Plan=0, Spotpris=605 < median 778 – markedsstyrt
2025-02-02 04:00 | 0 | 0 | 0 | 633.62 | ReserveShutdown | 0.55 | M1-MarketDriven | Elhub=0, Plan=0, Spotpris=634 < median 778 – markedsstyrt
2025-02-02 05:00 | 0 | 0 | 0 | 856.6 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=857 ≥ median 778 – uvanlig
2025-02-02 06:00 | 0 | 0 | 0 | 1470.45 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1470 ≥ median 778 – uvanlig
2025-02-02 07:00 | 0 | 0 | 0 | 1554.68 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1555 ≥ median 778 – uvanlig
2025-02-02 08:00 | 0 | 0 | 0 | 1559.13 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1559 ≥ median 778 – uvanlig
2025-02-02 09:00 | 0 | 0 | 0 | 1472.2 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1472 ≥ median 778 – uvanlig
2025-02-02 10:00 | 0 | 0 | 0 | 1463.9 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1464 ≥ median 778 – uvanlig
2025-02-02 11:00 | 0 | 0 | 0 | 1383.64 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1384 ≥ median 778 – uvanlig
2025-02-02 12:00 | 0 | 0 | 0 | 1266.3 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1266 ≥ median 778 – uvanlig
2025-02-02 13:00 | 0 | 0 | 0 | 1305.73 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1306 ≥ median 778 – uvanlig
2025-02-02 14:00 | 0.019936 | 0 | 0 | 1448.69 | InService | 0.8 | 0-Normal | Elhub=0.020 (ingen plan-sammenligning)
2025-02-02 15:00 | 0.4575 | 2.1 | 2.2 | 1712.15 | ForcedDerating | 0.65 | D1-ForcedDerating | Elhub=0.458 = 22% av Plan=2.100 – redusert kapasitet
2025-02-02 16:00 | 0.10188 | 2.1 | 2.2 | 1861.19 | ForcedDerating | 0.65 | D1-ForcedDerating | Elhub=0.102 = 5% av Plan=2.100 – redusert kapasitet
2025-02-02 17:00 | 0.05812 | 2.1 | 2.2 | 1953.5 | ForcedDerating | 0.65 | D1-ForcedDerating | Elhub=0.058 = 3% av Plan=2.100 – redusert kapasitet
2025-02-02 18:00 | 0 | 2.1 | 2.2 | 1962.74 | ForcedOutage | 0.8 | U1-UnplannedStop | Plan=2.100 men Elhub=0 (uvarslet stans)
2025-02-02 19:00 | 0 | 2.1 | 2.2 | 1874.18 | ForcedOutage | 0.8 | U1-UnplannedStop | Plan=2.100 men Elhub=0 (uvarslet stans)
2025-02-02 20:00 | 0 | 0 | 2.2 | 1474.31 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1474 ≥ median 778 – uvanlig
2025-02-02 21:00 | 0 | 0 | 1.8 | 995.58 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=996 ≥ median 778 – uvanlig
2025-02-02 22:00 | 0 | 0 | 0 | 731.19 | ReserveShutdown | 0.55 | M1-MarketDriven | Elhub=0, Plan=0, Spotpris=731 < median 778 – markedsstyrt
2025-02-02 23:00 | 0 | 0 | 0 | 829.58 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=830 ≥ median 778 – uvanlig
2025-02-03 | 0 | 0 | 0 | 668.01 | ReserveShutdown | 0.55 | M1-MarketDriven | Elhub=0, Plan=0, Spotpris=668 < median 778 – markedsstyrt
2025-02-03 01:00 | 0 | 0 | 0 | 667.43 | ReserveShutdown | 0.55 | M1-MarketDriven | Elhub=0, Plan=0, Spotpris=667 < median 778 – markedsstyrt
2025-02-03 02:00 | 0 | 0 | 0 | 655.49 | ReserveShutdown | 0.55 | M1-MarketDriven | Elhub=0, Plan=0, Spotpris=655 < median 778 – markedsstyrt
2025-02-03 03:00 | 0 | 0 | 0 | 687.2 | ReserveShutdown | 0.55 | M1-MarketDriven | Elhub=0, Plan=0, Spotpris=687 < median 778 – markedsstyrt
2025-02-03 04:00 | 0 | 0 | 0 | 906.79 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=907 ≥ median 778 – uvanlig
2025-02-03 05:00 | 0 | 0 | 0 | 1791.35 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1791 ≥ median 778 – uvanlig
2025-02-03 06:00 | 0 | 0 | 0 | 2316.75 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=2317 ≥ median 778 – uvanlig
2025-02-03 07:00 | 0 | 0 | 2.2 | 2626.19 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=2626 ≥ median 778 – uvanlig
2025-02-03 08:00 | 0 | 0 | 2.2 | 2064.41 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=2064 ≥ median 778 – uvanlig
2025-02-03 09:00 | 0 | 0 | 2.2 | 1706.88 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1707 ≥ median 778 – uvanlig
2025-02-03 10:00 | 0 | 2.1 | 2.2 | 1420.02 | ForcedOutage | 0.8 | U1-UnplannedStop | Plan=2.100 men Elhub=0 (uvarslet stans)
2025-02-03 11:00 | 0 | 2.1 | 2.2 | 1314.38 | ForcedOutage | 0.8 | U1-UnplannedStop | Plan=2.100 men Elhub=0 (uvarslet stans)
2025-02-03 12:00 | 0 | 2.1 | 2.2 | 1300.69 | ForcedOutage | 0.8 | U1-UnplannedStop | Plan=2.100 men Elhub=0 (uvarslet stans)
2025-02-03 13:00 | 0.008 | 0 | 2.2 | 1390.78 | InService | 0.8 | 0-Normal | Elhub=0.008 (ingen plan-sammenligning)
2025-02-03 14:00 | 0 | 0 | 2.2 | 1501.33 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1501 ≥ median 778 – uvanlig
2025-02-03 15:00 | 0 | 2.1 | 2.2 | 1926.71 | ForcedOutage | 0.8 | U1-UnplannedStop | Plan=2.100 men Elhub=0 (uvarslet stans)
2025-02-03 16:00 | 0 | 0 | 2.2 | 2324.01 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=2324 ≥ median 778 – uvanlig
2025-02-03 17:00 | 0 | 0 | 2.2 | 2276.16 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=2276 ≥ median 778 – uvanlig
2025-02-03 18:00 | 0 | 0 | 2.2 | 2268.44 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=2268 ≥ median 778 – uvanlig
2025-02-03 19:00 | 0 | 0 | 2.2 | 1896.76 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1897 ≥ median 778 – uvanlig
2025-02-03 20:00 | 0 | 0 | 2.2 | 1579.25 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1579 ≥ median 778 – uvanlig
2025-02-03 21:00 | 0 | 0 | 2 | 1238.34 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1238 ≥ median 778 – uvanlig
2025-02-03 22:00 | 0 | 0 | 0 | 689.66 | ReserveShutdown | 0.55 | M1-MarketDriven | Elhub=0, Plan=0, Spotpris=690 < median 778 – markedsstyrt
2025-02-03 23:00 | 0 | 0 | 0 | 701.64 | ReserveShutdown | 0.55 | M1-MarketDriven | Elhub=0, Plan=0, Spotpris=702 < median 778 – markedsstyrt
2025-02-04 | 0 | 0 | 0 | 626.14 | ReserveShutdown | 0.55 | M1-MarketDriven | Elhub=0, Plan=0, Spotpris=626 < median 778 – markedsstyrt
2025-02-04 01:00 | 0 | 0 | 0 | 616.19 | ReserveShutdown | 0.55 | M1-MarketDriven | Elhub=0, Plan=0, Spotpris=616 < median 778 – markedsstyrt
2025-02-04 02:00 | 0 | 0 | 0 | 593.83 | ReserveShutdown | 0.55 | M1-MarketDriven | Elhub=0, Plan=0, Spotpris=594 < median 778 – markedsstyrt
2025-02-04 03:00 | 0 | 0 | 1.5 | 584.7 | ReserveShutdown | 0.55 | M1-MarketDriven | Elhub=0, Plan=0, Spotpris=585 < median 778 – markedsstyrt
2025-02-04 04:00 | 0 | 0 | 1.5 | 607.18 | ReserveShutdown | 0.55 | M1-MarketDriven | Elhub=0, Plan=0, Spotpris=607 < median 778 – markedsstyrt
2025-02-04 05:00 | 0 | 0 | 1.9 | 942.9 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=943 ≥ median 778 – uvanlig
2025-02-04 06:00 | 0 | 0 | 2.2 | 1746.61 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1747 ≥ median 778 – uvanlig
2025-02-04 07:00 | 0 | 0 | 2.2 | 2190.26 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=2190 ≥ median 778 – uvanlig
2025-02-04 08:00 | 0 | 0 | 2.2 | 1636.82 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1637 ≥ median 778 – uvanlig
2025-02-04 09:00 | 0 | 0 | 2.2 | 1519.99 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1520 ≥ median 778 – uvanlig
2025-02-04 10:00 | 0.43786 | 0 | 2.2 | 1200.19 | InService | 0.8 | 0-Normal | Elhub=0.438 (ingen plan-sammenligning)
2025-02-04 11:00 | 1.997 | 0 | 2.2 | 980.24 | InService | 0.8 | 0-Normal | Elhub=1.997 (ingen plan-sammenligning)
2025-02-04 12:00 | 1.9992 | 0 | 2.2 | 810.74 | InService | 0.8 | 0-Normal | Elhub=1.999 (ingen plan-sammenligning)
2025-02-04 13:00 | 1.9991 | 0 | 2.2 | 628.01 | InService | 0.8 | 0-Normal | Elhub=1.999 (ingen plan-sammenligning)
2025-02-04 14:00 | 1.9974 | 0 | 2.2 | 617.95 | InService | 0.8 | 0-Normal | Elhub=1.997 (ingen plan-sammenligning)
2025-02-04 15:00 | 2.0004 | 2.1 | 2.2 | 633.87 | InService | 0.95 | 0-Normal | Elhub=2.000 ≈ Plan=2.100 (ratio=95%)
2025-02-04 16:00 | 1.9995 | 2.1 | 2.2 | 673.9 | InService | 0.95 | 0-Normal | Elhub=1.999 ≈ Plan=2.100 (ratio=95%)
2025-02-04 17:00 | 2.1333 | 2.1 | 2.2 | 625.44 | InService | 0.95 | 0-Normal | Elhub=2.133 ≈ Plan=2.100 (ratio=102%)
2025-02-04 18:00 | 2.1918 | 2.1 | 2.2 | 589.03 | InService | 0.95 | 0-Normal | Elhub=2.192 ≈ Plan=2.100 (ratio=104%)
2025-02-04 19:00 | 2.1913 | 2.1 | 0 | 558.36 | InService | 0.95 | 0-Normal | Elhub=2.191 ≈ Plan=2.100 (ratio=104%)
2025-02-04 20:00 | 2.193 | 2.1 | 0 | 533.67 | InService | 0.95 | 0-Normal | Elhub=2.193 ≈ Plan=2.100 (ratio=104%)
2025-02-04 21:00 | 2.1414 | 2.1 | 0 | 479.47 | InService | 0.95 | 0-Normal | Elhub=2.141 ≈ Plan=2.100 (ratio=102%)
2025-02-04 22:00 | 1.7531 | 1.7 | 0 | 462.73 | InService | 0.95 | 0-Normal | Elhub=1.753 ≈ Plan=1.700 (ratio=103%)
2025-02-04 23:00 | 1.7355 | 1.7 | 1.7 | 497.02 | InService | 0.95 | 0-Normal | Elhub=1.736 ≈ Plan=1.700 (ratio=102%)
2025-02-05 | 1.7369 | 1.7 | 1.7 | 487.88 | InService | 0.95 | 0-Normal | Elhub=1.737 ≈ Plan=1.700 (ratio=102%)
2025-02-05 01:00 | 2.1562 | 1.7 | 1.7 | 486.24 | InService | 0.95 | 0-Normal | Elhub=2.156 ≈ Plan=1.700 (ratio=127%)
2025-02-05 02:00 | 2.1811 | 2.1 | 1.7 | 488.23 | InService | 0.95 | 0-Normal | Elhub=2.181 ≈ Plan=2.100 (ratio=104%)
2025-02-05 03:00 | 2.1801 | 2.1 | 2.1 | 482.95 | InService | 0.95 | 0-Normal | Elhub=2.180 ≈ Plan=2.100 (ratio=104%)
2025-02-05 04:00 | 2.1814 | 2.1 | 2.1 | 474.63 | InService | 0.95 | 0-Normal | Elhub=2.181 ≈ Plan=2.100 (ratio=104%)
2025-02-05 05:00 | 2.1814 | 2.1 | 2.1 | 519.18 | InService | 0.95 | 0-Normal | Elhub=2.181 ≈ Plan=2.100 (ratio=104%)
2025-02-05 06:00 | 2.1815 | 2.1 | 2.1 | 543.69 | InService | 0.95 | 0-Normal | Elhub=2.181 ≈ Plan=2.100 (ratio=104%)
2025-02-05 07:00 | 2.1804 | 2.1 | 2.2 | 559.99 | InService | 0.95 | 0-Normal | Elhub=2.180 ≈ Plan=2.100 (ratio=104%)
2025-02-05 08:00 | 2.1826 | 2.1 | 2.2 | 557.53 | InService | 0.95 | 0-Normal | Elhub=2.183 ≈ Plan=2.100 (ratio=104%)
2025-02-05 09:00 | 2.1815 | 2.1 | 2.2 | 563.51 | InService | 0.95 | 0-Normal | Elhub=2.182 ≈ Plan=2.100 (ratio=104%)
2025-02-05 10:00 | 2.1816 | 2.1 | 2.2 | 558.46 | InService | 0.95 | 0-Normal | Elhub=2.182 ≈ Plan=2.100 (ratio=104%)
2025-02-05 11:00 | 2.1815 | 2.1 | 2.1 | 547.32 | InService | 0.95 | 0-Normal | Elhub=2.181 ≈ Plan=2.100 (ratio=104%)
2025-02-05 12:00 | 2.1818 | 2.1 | 2.1 | 547.21 | InService | 0.95 | 0-Normal | Elhub=2.182 ≈ Plan=2.100 (ratio=104%)
2025-02-05 13:00 | 2.1824 | 2.1 | 2.1 | 543.57 | InService | 0.95 | 0-Normal | Elhub=2.182 ≈ Plan=2.100 (ratio=104%)
2025-02-05 14:00 | 2.1821 | 2.1 | 2.1 | 553.19 | InService | 0.95 | 0-Normal | Elhub=2.182 ≈ Plan=2.100 (ratio=104%)
2025-02-05 15:00 | 2.1821 | 2.1 | 2.2 | 655.66 | InService | 0.95 | 0-Normal | Elhub=2.182 ≈ Plan=2.100 (ratio=104%)
2025-02-05 16:00 | 2.1818 | 2.1 | 2.2 | 711.71 | InService | 0.95 | 0-Normal | Elhub=2.182 ≈ Plan=2.100 (ratio=104%)
2025-02-05 17:00 | 2.1824 | 2.1 | 2.2 | 733.64 | InService | 0.95 | 0-Normal | Elhub=2.182 ≈ Plan=2.100 (ratio=104%)
2025-02-05 18:00 | 2.1802 | 2.1 | 2.2 | 662.46 | InService | 0.95 | 0-Normal | Elhub=2.180 ≈ Plan=2.100 (ratio=104%)
2025-02-05 19:00 | 2.1827 | 2.1 | 0 | 591.41 | InService | 0.95 | 0-Normal | Elhub=2.183 ≈ Plan=2.100 (ratio=104%)
2025-02-05 20:00 | 2.1827 | 2.1 | 1.8 | 633.03 | InService | 0.95 | 0-Normal | Elhub=2.183 ≈ Plan=2.100 (ratio=104%)
2025-02-05 21:00 | 2.1826 | 2.1 | 0 | 571.36 | InService | 0.95 | 0-Normal | Elhub=2.183 ≈ Plan=2.100 (ratio=104%)
2025-02-05 22:00 | 2.1818 | 2.1 | 0 | 548.73 | InService | 0.95 | 0-Normal | Elhub=2.182 ≈ Plan=2.100 (ratio=104%)
2025-02-05 23:00 | 2.1854 | 2.2 | 2.2 | 572.62 | InService | 0.95 | 0-Normal | Elhub=2.185 ≈ Plan=2.200 (ratio=99%)
2025-02-06 | 2.1825 | 2.12 | 2.2 | 566.43 | InService | 0.95 | 0-Normal | Elhub=2.183 ≈ Plan=2.120 (ratio=103%)
2025-02-06 01:00 | 2.1832 | 2.099 | 2.2 | 567.72 | InService | 0.95 | 0-Normal | Elhub=2.183 ≈ Plan=2.099 (ratio=104%)
2025-02-06 02:00 | 2.182 | 2.078 | 2.2 | 569.35 | InService | 0.95 | 0-Normal | Elhub=2.182 ≈ Plan=2.078 (ratio=105%)
2025-02-06 03:00 | 2.1834 | 2.057 | 2.2 | 573.09 | InService | 0.95 | 0-Normal | Elhub=2.183 ≈ Plan=2.057 (ratio=106%)
2025-02-06 04:00 | 2.1815 | 2.036 | 2.2 | 627.64 | InService | 0.95 | 0-Normal | Elhub=2.182 ≈ Plan=2.036 (ratio=107%)
2025-02-06 05:00 | 2.1818 | 2.016 | 2.2 | 896.43 | InService | 0.95 | 0-Normal | Elhub=2.182 ≈ Plan=2.016 (ratio=108%)
2025-02-06 06:00 | 2.1808 | 1.996 | 2.2 | 1810.15 | InService | 0.95 | 0-Normal | Elhub=2.181 ≈ Plan=1.996 (ratio=109%)
2025-02-06 07:00 | 2.1818 | 2.103 | 2.2 | 2256.03 | InService | 0.95 | 0-Normal | Elhub=2.182 ≈ Plan=2.103 (ratio=104%)
2025-02-06 08:00 | 2.1804 | 2.123 | 2.2 | 1993.2 | InService | 0.95 | 0-Normal | Elhub=2.180 ≈ Plan=2.123 (ratio=103%)
2025-02-06 09:00 | 2.1806 | 2.113 | 2.2 | 1765.29 | InService | 0.95 | 0-Normal | Elhub=2.181 ≈ Plan=2.113 (ratio=103%)
2025-02-06 10:00 | 2.1803 | 2.121 | 2.2 | 1375.6 | InService | 0.95 | 0-Normal | Elhub=2.180 ≈ Plan=2.121 (ratio=103%)
2025-02-06 11:00 | 2.1785 | 2.2 | 2.2 | 1058.45 | InService | 0.95 | 0-Normal | Elhub=2.178 ≈ Plan=2.200 (ratio=99%)
2025-02-06 12:00 | 2.1797 | 2.2 | 2.2 | 893.63 | InService | 0.95 | 0-Normal | Elhub=2.180 ≈ Plan=2.200 (ratio=99%)
2025-02-06 13:00 | 2.181 | 2.2 | 2.2 | 836.62 | InService | 0.95 | 0-Normal | Elhub=2.181 ≈ Plan=2.200 (ratio=99%)
2025-02-06 14:00 | 2.1807 | 2.2 | 2.2 | 1077.26 | InService | 0.95 | 0-Normal | Elhub=2.181 ≈ Plan=2.200 (ratio=99%)
2025-02-06 15:00 | 2.181 | 2.2 | 2.2 | 1397.21 | InService | 0.95 | 0-Normal | Elhub=2.181 ≈ Plan=2.200 (ratio=99%)
2025-02-06 16:00 | 2.1796 | 2.2 | 2.2 | 1928.48 | InService | 0.95 | 0-Normal | Elhub=2.180 ≈ Plan=2.200 (ratio=99%)
2025-02-06 17:00 | 2.1795 | 2.2 | 2.2 | 1927.08 | InService | 0.95 | 0-Normal | Elhub=2.179 ≈ Plan=2.200 (ratio=99%)
2025-02-06 18:00 | 2.1783 | 2.2 | 2.2 | 1838.89 | InService | 0.95 | 0-Normal | Elhub=2.178 ≈ Plan=2.200 (ratio=99%)
2025-02-06 19:00 | 2.1778 | 2.2 | 2.2 | 1585.63 | InService | 0.95 | 0-Normal | Elhub=2.178 ≈ Plan=2.200 (ratio=99%)
2025-02-06 20:00 | 2.1774 | 2.2 | 2.2 | 1430.85 | InService | 0.95 | 0-Normal | Elhub=2.177 ≈ Plan=2.200 (ratio=99%)
2025-02-06 21:00 | 2.1761 | 2.2 | 2.2 | 852.63 | InService | 0.95 | 0-Normal | Elhub=2.176 ≈ Plan=2.200 (ratio=99%)
2025-02-06 22:00 | 2.1747 | 2.2 | 2.2 | 728.1 | InService | 0.95 | 0-Normal | Elhub=2.175 ≈ Plan=2.200 (ratio=99%)
2025-02-06 23:00 | 2.1759 | 2.2 | 2.2 | 770.69 | InService | 0.95 | 0-Normal | Elhub=2.176 ≈ Plan=2.200 (ratio=99%)
2025-02-07 | 2.1768 | 2.105 | 2.2 | 710.66 | InService | 0.95 | 0-Normal | Elhub=2.177 ≈ Plan=2.105 (ratio=103%)
2025-02-07 01:00 | 2.174 | 2.084 | 2.2 | 703.32 | InService | 0.95 | 0-Normal | Elhub=2.174 ≈ Plan=2.084 (ratio=104%)
2025-02-07 02:00 | 2.1749 | 2.063 | 2.2 | 690.5 | InService | 0.95 | 0-Normal | Elhub=2.175 ≈ Plan=2.063 (ratio=105%)
2025-02-07 03:00 | 2.1747 | 2.042 | 2.2 | 697.84 | InService | 0.95 | 0-Normal | Elhub=2.175 ≈ Plan=2.042 (ratio=106%)
2025-02-07 04:00 | 2.1747 | 2.022 | 2.2 | 727.45 | InService | 0.95 | 0-Normal | Elhub=2.175 ≈ Plan=2.022 (ratio=108%)
2025-02-07 05:00 | 2.1733 | 2.002 | 2.2 | 1237.51 | InService | 0.95 | 0-Normal | Elhub=2.173 ≈ Plan=2.002 (ratio=109%)
2025-02-07 06:00 | 2.1737 | 1.982 | 2.2 | 1597.92 | InService | 0.95 | 0-Normal | Elhub=2.174 ≈ Plan=1.982 (ratio=110%)
2025-02-07 07:00 | 2.1731 | 2.093 | 2.2 | 1852.25 | InService | 0.95 | 0-Normal | Elhub=2.173 ≈ Plan=2.093 (ratio=104%)
2025-02-07 08:00 | 2.1723 | 2.105 | 2.2 | 1694.54 | InService | 0.95 | 0-Normal | Elhub=2.172 ≈ Plan=2.105 (ratio=103%)
2025-02-07 09:00 | 2.1712 | 2.099 | 2.2 | 1431.59 | InService | 0.95 | 0-Normal | Elhub=2.171 ≈ Plan=2.099 (ratio=103%)
2025-02-07 10:00 | 2.1701 | 2.098 | 2.2 | 1033.42 | InService | 0.95 | 0-Normal | Elhub=2.170 ≈ Plan=2.098 (ratio=103%)
2025-02-07 11:00 | 2.1691 | 2.2 | 2.2 | 959.52 | InService | 0.95 | 0-Normal | Elhub=2.169 ≈ Plan=2.200 (ratio=99%)
2025-02-07 12:00 | 2.169 | 2.2 | 2.2 | 1005.33 | InService | 0.95 | 0-Normal | Elhub=2.169 ≈ Plan=2.200 (ratio=99%)
2025-02-07 13:00 | 2.1692 | 2.2 | 2.2 | 985.28 | InService | 0.95 | 0-Normal | Elhub=2.169 ≈ Plan=2.200 (ratio=99%)
2025-02-07 14:00 | 2.1681 | 2.2 | 2.2 | 911.15 | InService | 0.95 | 0-Normal | Elhub=2.168 ≈ Plan=2.200 (ratio=99%)
2025-02-07 15:00 | 2.1672 | 2.2 | 2.2 | 990.87 | InService | 0.95 | 0-Normal | Elhub=2.167 ≈ Plan=2.200 (ratio=99%)
2025-02-07 16:00 | 2.1677 | 2.2 | 2.2 | 1025.37 | InService | 0.95 | 0-Normal | Elhub=2.168 ≈ Plan=2.200 (ratio=99%)
2025-02-07 17:00 | 2.1638 | 2.2 | 2.2 | 984.7 | InService | 0.95 | 0-Normal | Elhub=2.164 ≈ Plan=2.200 (ratio=98%)
2025-02-07 18:00 | 2.166 | 2.2 | 2.2 | 814.52 | InService | 0.95 | 0-Normal | Elhub=2.166 ≈ Plan=2.200 (ratio=98%)
2025-02-07 19:00 | 1.8459 | 1.8 | 1.8 | 659.84 | InService | 0.95 | 0-Normal | Elhub=1.846 ≈ Plan=1.800 (ratio=103%)
2025-02-07 20:00 | 1.838 | 1.8 | 1.8 | 635.72 | InService | 0.95 | 0-Normal | Elhub=1.838 ≈ Plan=1.800 (ratio=102%)
2025-02-07 21:00 | 1.8363 | 1.8 | 1.8 | 615.09 | InService | 0.95 | 0-Normal | Elhub=1.836 ≈ Plan=1.800 (ratio=102%)
2025-02-07 22:00 | 1.8364 | 1.8 | 1.8 | 587.58 | InService | 0.95 | 0-Normal | Elhub=1.836 ≈ Plan=1.800 (ratio=102%)
2025-02-07 23:00 | 0.020834 | 0 | 0 | 577.07 | InService | 0.8 | 0-Normal | Elhub=0.021 (ingen plan-sammenligning)
2025-02-08 | 0 | 1.787 | 0 | 569.74 | ForcedOutage | 0.8 | U1-UnplannedStop | Plan=1.787 men Elhub=0 (uvarslet stans)
2025-02-08 01:00 | 0 | 1.769 | 0 | 564.85 | ForcedOutage | 0.8 | U1-UnplannedStop | Plan=1.769 men Elhub=0 (uvarslet stans)
2025-02-08 02:00 | 0 | 1.751 | 0 | 560.77 | ForcedOutage | 0.8 | U1-UnplannedStop | Plan=1.751 men Elhub=0 (uvarslet stans)
2025-02-08 03:00 | 0 | 1.733 | 0 | 558.91 | ForcedOutage | 0.8 | U1-UnplannedStop | Plan=1.733 men Elhub=0 (uvarslet stans)
2025-02-08 04:00 | 0 | 1.716 | 0 | 559.84 | ForcedOutage | 0.8 | U1-UnplannedStop | Plan=1.716 men Elhub=0 (uvarslet stans)
2025-02-08 05:00 | 0 | 1.699 | 0 | 566.71 | ForcedOutage | 0.8 | U1-UnplannedStop | Plan=1.699 men Elhub=0 (uvarslet stans)
2025-02-08 06:00 | 0 | 1.682 | 0 | 576.37 | ForcedOutage | 0.8 | U1-UnplannedStop | Plan=1.682 men Elhub=0 (uvarslet stans)
2025-02-08 07:00 | 0 | 0 | 0 | 580.8 | ReserveShutdown | 0.55 | M1-MarketDriven | Elhub=0, Plan=0, Spotpris=581 < median 778 – markedsstyrt
2025-02-08 08:00 | 0 | 0 | 0 | 606.53 | ReserveShutdown | 0.55 | M1-MarketDriven | Elhub=0, Plan=0, Spotpris=607 < median 778 – markedsstyrt
2025-02-08 09:00 | 0 | 0 | 0 | 607.46 | ReserveShutdown | 0.55 | M1-MarketDriven | Elhub=0, Plan=0, Spotpris=607 < median 778 – markedsstyrt
2025-02-08 10:00 | 0.013792 | 0 | 0 | 601.29 | InService | 0.8 | 0-Normal | Elhub=0.014 (ingen plan-sammenligning)
2025-02-08 11:00 | 0.60784 | 0.6 | 0.6 | 611.19 | InService | 0.95 | 0-Normal | Elhub=0.608 ≈ Plan=0.600 (ratio=101%)
2025-02-08 12:00 | 0.60912 | 0.6 | 0.6 | 603.15 | InService | 0.95 | 0-Normal | Elhub=0.609 ≈ Plan=0.600 (ratio=102%)
2025-02-08 13:00 | 0.61347 | 0.6 | 0.6 | 617.82 | InService | 0.95 | 0-Normal | Elhub=0.613 ≈ Plan=0.600 (ratio=102%)
2025-02-08 14:00 | 0.61709 | 0.6 | 0.6 | 658.81 | InService | 0.95 | 0-Normal | Elhub=0.617 ≈ Plan=0.600 (ratio=103%)
2025-02-08 15:00 | 2.1384 | 2.2 | 2.2 | 801.1 | InService | 0.95 | 0-Normal | Elhub=2.138 ≈ Plan=2.200 (ratio=97%)
2025-02-08 16:00 | 2.1947 | 2.2 | 2.2 | 1094.53 | InService | 0.95 | 0-Normal | Elhub=2.195 ≈ Plan=2.200 (ratio=100%)
2025-02-08 17:00 | 2.1836 | 2.2 | 2.2 | 1059.01 | InService | 0.95 | 0-Normal | Elhub=2.184 ≈ Plan=2.200 (ratio=99%)
2025-02-08 18:00 | 2.1816 | 2.2 | 2.2 | 882.37 | InService | 0.95 | 0-Normal | Elhub=2.182 ≈ Plan=2.200 (ratio=99%)
2025-02-08 19:00 | 1.8528 | 1.7 | 1.7 | 878.65 | InService | 0.95 | 0-Normal | Elhub=1.853 ≈ Plan=1.700 (ratio=109%)
2025-02-08 20:00 | 0.74132 | 0.7 | 0.7 | 706.9 | InService | 0.95 | 0-Normal | Elhub=0.741 ≈ Plan=0.700 (ratio=106%)
2025-02-08 21:00 | 0.71126 | 0.7 | 0.7 | 736.36 | InService | 0.95 | 0-Normal | Elhub=0.711 ≈ Plan=0.700 (ratio=102%)
2025-02-08 22:00 | 0.71149 | 0.7 | 0.7 | 691.53 | InService | 0.95 | 0-Normal | Elhub=0.711 ≈ Plan=0.700 (ratio=102%)
2025-02-08 23:00 | 1.3094 | 1.3 | 1.3 | 638.78 | InService | 0.95 | 0-Normal | Elhub=1.309 ≈ Plan=1.300 (ratio=101%)
2025-02-09 | 1.3258 | 0.689 | 1.3 | 625.89 | InService | 0.95 | 0-Normal | Elhub=1.326 ≈ Plan=0.689 (ratio=192%)
2025-02-09 01:00 | 1.3244 | 0.682 | 1.3 | 625.43 | InService | 0.95 | 0-Normal | Elhub=1.324 ≈ Plan=0.682 (ratio=194%)
2025-02-09 02:00 | 1.3244 | 0.675 | 1.3 | 627.29 | InService | 0.95 | 0-Normal | Elhub=1.324 ≈ Plan=0.675 (ratio=196%)
2025-02-09 03:00 | 0.015366 | 0.668 | 0 | 632.16 | ForcedDerating | 0.65 | D1-ForcedDerating | Elhub=0.015 = 2% av Plan=0.668 – redusert kapasitet
2025-02-09 04:00 | 0 | 0.662 | 0 | 668.27 | ForcedOutage | 0.8 | U1-UnplannedStop | Plan=0.662 men Elhub=0 (uvarslet stans)
2025-02-09 05:00 | 0 | 0.655 | 0 | 771.94 | ForcedOutage | 0.8 | U1-UnplannedStop | Plan=0.655 men Elhub=0 (uvarslet stans)
2025-02-09 06:00 | 0.024256 | 0.649 | 0 | 915.68 | ForcedDerating | 0.65 | D1-ForcedDerating | Elhub=0.024 = 4% av Plan=0.649 – redusert kapasitet
2025-02-09 07:00 | 1.9265 | 1.28 | 1.9 | 907.32 | InService | 0.95 | 0-Normal | Elhub=1.927 ≈ Plan=1.280 (ratio=151%)
2025-02-09 08:00 | 2.0338 | 1.28 | 2 | 1295.79 | InService | 0.95 | 0-Normal | Elhub=2.034 ≈ Plan=1.280 (ratio=159%)
2025-02-09 09:00 | 2.0383 | 1.901 | 2 | 1227.87 | InService | 0.95 | 0-Normal | Elhub=2.038 ≈ Plan=1.901 (ratio=107%)
2025-02-09 10:00 | 1.9417 | 1.971 | 1.9 | 1160.41 | InService | 0.95 | 0-Normal | Elhub=1.942 ≈ Plan=1.971 (ratio=99%)
2025-02-09 11:00 | 2.1807 | 2.2 | 2.2 | 967.57 | InService | 0.95 | 0-Normal | Elhub=2.181 ≈ Plan=2.200 (ratio=99%)
2025-02-09 12:00 | 2.1877 | 2.2 | 2.2 | 922.64 | InService | 0.95 | 0-Normal | Elhub=2.188 ≈ Plan=2.200 (ratio=99%)
2025-02-09 13:00 | 2.1871 | 2.2 | 2.2 | 922.29 | InService | 0.95 | 0-Normal | Elhub=2.187 ≈ Plan=2.200 (ratio=99%)
2025-02-09 14:00 | 2.1848 | 2.2 | 2.2 | 1098.42 | InService | 0.95 | 0-Normal | Elhub=2.185 ≈ Plan=2.200 (ratio=99%)
2025-02-09 15:00 | 2.1859 | 2.2 | 2.2 | 1234.02 | InService | 0.95 | 0-Normal | Elhub=2.186 ≈ Plan=2.200 (ratio=99%)
2025-02-09 16:00 | 2.1838 | 2.2 | 2.2 | 1226.01 | InService | 0.95 | 0-Normal | Elhub=2.184 ≈ Plan=2.200 (ratio=99%)
2025-02-09 17:00 | 2.183 | 2.2 | 2.2 | 1213.59 | InService | 0.95 | 0-Normal | Elhub=2.183 ≈ Plan=2.200 (ratio=99%)
2025-02-09 18:00 | 2.1817 | 2.2 | 2.2 | 1061.26 | InService | 0.95 | 0-Normal | Elhub=2.182 ≈ Plan=2.200 (ratio=99%)
2025-02-09 19:00 | 0.034052 | 0 | 0 | 844.16 | InService | 0.8 | 0-Normal | Elhub=0.034 (ingen plan-sammenligning)
2025-02-09 20:00 | 0 | 0 | 0 | 786.81 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=787 ≥ median 778 – uvanlig
2025-02-09 21:00 | 0 | 0 | 0 | 714.71 | ReserveShutdown | 0.55 | M1-MarketDriven | Elhub=0, Plan=0, Spotpris=715 < median 778 – markedsstyrt
2025-02-09 22:00 | 0 | 0 | 0 | 660.49 | ReserveShutdown | 0.55 | M1-MarketDriven | Elhub=0, Plan=0, Spotpris=660 < median 778 – markedsstyrt
2025-02-09 23:00 | 0 | 0 | 0 | 650.16 | ReserveShutdown | 0.55 | M1-MarketDriven | Elhub=0, Plan=0, Spotpris=650 < median 778 – markedsstyrt
2025-02-10 | 0 | 2.121 | 0 | 638.43 | ForcedOutage | 0.8 | U1-UnplannedStop | Plan=2.121 men Elhub=0 (uvarslet stans)
2025-02-10 01:00 | 0 | 2.1 | 0 | 625.66 | ForcedOutage | 0.8 | U1-UnplannedStop | Plan=2.100 men Elhub=0 (uvarslet stans)
2025-02-10 02:00 | 0 | 2.079 | 0 | 622.76 | ForcedOutage | 0.8 | U1-UnplannedStop | Plan=2.079 men Elhub=0 (uvarslet stans)
2025-02-10 03:00 | 0 | 2.058 | 0 | 623.69 | ForcedOutage | 0.8 | U1-UnplannedStop | Plan=2.058 men Elhub=0 (uvarslet stans)
2025-02-10 04:00 | 0 | 2.037 | 0 | 639.24 | ForcedOutage | 0.8 | U1-UnplannedStop | Plan=2.037 men Elhub=0 (uvarslet stans)
2025-02-10 05:00 | 0 | 2.017 | 0 | 695.2 | ForcedOutage | 0.8 | U1-UnplannedStop | Plan=2.017 men Elhub=0 (uvarslet stans)
2025-02-10 06:00 | 0.013728 | 1.997 | 0 | 1140.79 | ForcedDerating | 0.65 | D1-ForcedDerating | Elhub=0.014 = 1% av Plan=1.997 – redusert kapasitet
2025-02-10 07:00 | 1.8224 | 0 | 1.8 | 1252.83 | InService | 0.8 | 0-Normal | Elhub=1.822 (ingen plan-sammenligning)
2025-02-10 08:00 | 1.8362 | 0 | 1.8 | 1182.94 | InService | 0.8 | 0-Normal | Elhub=1.836 (ingen plan-sammenligning)
2025-02-10 09:00 | 0.62969 | 1.794 | 0 | 1028.99 | ForcedDerating | 0.65 | D1-ForcedDerating | Elhub=0.630 = 35% av Plan=1.794 – redusert kapasitet
2025-02-10 10:00 | 0.6041 | 1.784 | 0 | 781.58 | ForcedDerating | 0.65 | D1-ForcedDerating | Elhub=0.604 = 34% av Plan=1.784 – redusert kapasitet
2025-02-10 11:00 | 1.3093 | 1.3 | 1.3 | 723.07 | InService | 0.95 | 0-Normal | Elhub=1.309 ≈ Plan=1.300 (ratio=101%)
2025-02-10 12:00 | 1.0187 | 1.3 | 1.3 | 664.9 | ForcedDerating | 0.65 | D1-ForcedDerating | Elhub=1.019 = 78% av Plan=1.300 – redusert kapasitet
2025-02-10 13:00 | 1.3269 | 1.3 | 1.3 | 675.7 | InService | 0.95 | 0-Normal | Elhub=1.327 ≈ Plan=1.300 (ratio=102%)
2025-02-10 14:00 | 1.3289 | 1.3 | 1.3 | 671.17 | InService | 0.95 | 0-Normal | Elhub=1.329 ≈ Plan=1.300 (ratio=102%)
2025-02-10 15:00 | 0.011176 | 0 | 0 | 749.42 | InService | 0.8 | 0-Normal | Elhub=0.011 (ingen plan-sammenligning)
2025-02-10 16:00 | 0 | 0 | 0 | 774.03 | PlannedOutage | 0.7 | P1-ScheduledStop | Elhub=0 sammenhengende 34h (≥ 24h), sannsynlig planlagt
2025-02-10 17:00 | 0 | 0 | 0 | 782.05 | PlannedOutage | 0.7 | P1-ScheduledStop | Elhub=0 sammenhengende 34h (≥ 24h), sannsynlig planlagt
2025-02-10 18:00 | 0 | 0 | 0 | 709.83 | PlannedOutage | 0.7 | P1-ScheduledStop | Elhub=0 sammenhengende 34h (≥ 24h), sannsynlig planlagt
2025-02-10 19:00 | 0 | 0 | 0 | 669.08 | PlannedOutage | 0.7 | P1-ScheduledStop | Elhub=0 sammenhengende 34h (≥ 24h), sannsynlig planlagt
2025-02-10 20:00 | 0 | 0 | 0 | 647.25 | PlannedOutage | 0.7 | P1-ScheduledStop | Elhub=0 sammenhengende 34h (≥ 24h), sannsynlig planlagt
2025-02-10 21:00 | 0 | 0 | 0 | 626.36 | PlannedOutage | 0.7 | P1-ScheduledStop | Elhub=0 sammenhengende 34h (≥ 24h), sannsynlig planlagt
2025-02-10 22:00 | 0 | 0 | 0 | 615.68 | PlannedOutage | 0.7 | P1-ScheduledStop | Elhub=0 sammenhengende 34h (≥ 24h), sannsynlig planlagt
2025-02-10 23:00 | 0 | 0 | 0 | 602.47 | PlannedOutage | 0.7 | P1-ScheduledStop | Elhub=0 sammenhengende 34h (≥ 24h), sannsynlig planlagt
2025-02-11 | 0 | 1.284 | 0 | 588.24 | ForcedOutage | 0.8 | U1-UnplannedStop | Plan=1.284 men Elhub=0 (uvarslet stans)
2025-02-11 01:00 | 0 | 1.271 | 0 | 583.61 | ForcedOutage | 0.8 | U1-UnplannedStop | Plan=1.271 men Elhub=0 (uvarslet stans)
2025-02-11 02:00 | 0 | 1.258 | 0 | 579.44 | ForcedOutage | 0.8 | U1-UnplannedStop | Plan=1.258 men Elhub=0 (uvarslet stans)
2025-02-11 03:00 | 0 | 1.246 | 0 | 581.41 | ForcedOutage | 0.8 | U1-UnplannedStop | Plan=1.246 men Elhub=0 (uvarslet stans)
2025-02-11 04:00 | 0 | 1.234 | 0 | 592.06 | ForcedOutage | 0.8 | U1-UnplannedStop | Plan=1.234 men Elhub=0 (uvarslet stans)
2025-02-11 05:00 | 0 | 1.222 | 0 | 641.83 | ForcedOutage | 0.8 | U1-UnplannedStop | Plan=1.222 men Elhub=0 (uvarslet stans)
2025-02-11 06:00 | 0 | 1.21 | 0 | 691.6 | ForcedOutage | 0.8 | U1-UnplannedStop | Plan=1.210 men Elhub=0 (uvarslet stans)
2025-02-11 07:00 | 0 | 0 | 0 | 855.62 | PlannedOutage | 0.7 | P1-ScheduledStop | Elhub=0 sammenhengende 34h (≥ 24h), sannsynlig planlagt
2025-02-11 08:00 | 0 | 0 | 0 | 736.74 | PlannedOutage | 0.7 | P1-ScheduledStop | Elhub=0 sammenhengende 34h (≥ 24h), sannsynlig planlagt
2025-02-11 09:00 | 0 | 0 | 0 | 694.49 | PlannedOutage | 0.7 | P1-ScheduledStop | Elhub=0 sammenhengende 34h (≥ 24h), sannsynlig planlagt
2025-02-11 10:00 | 0 | 0 | 0 | 686.39 | PlannedOutage | 0.7 | P1-ScheduledStop | Elhub=0 sammenhengende 34h (≥ 24h), sannsynlig planlagt
2025-02-11 11:00 | 0 | 0 | 0 | 662.08 | PlannedOutage | 0.7 | P1-ScheduledStop | Elhub=0 sammenhengende 34h (≥ 24h), sannsynlig planlagt
2025-02-11 12:00 | 0 | 0 | 0 | 645.18 | PlannedOutage | 0.7 | P1-ScheduledStop | Elhub=0 sammenhengende 34h (≥ 24h), sannsynlig planlagt
2025-02-11 13:00 | 0 | 0 | 0 | 644.72 | PlannedOutage | 0.7 | P1-ScheduledStop | Elhub=0 sammenhengende 34h (≥ 24h), sannsynlig planlagt
2025-02-11 14:00 | 0 | 0 | 0 | 654.68 | PlannedOutage | 0.7 | P1-ScheduledStop | Elhub=0 sammenhengende 34h (≥ 24h), sannsynlig planlagt
2025-02-11 15:00 | 0 | 0 | 0 | 691.02 | PlannedOutage | 0.7 | P1-ScheduledStop | Elhub=0 sammenhengende 34h (≥ 24h), sannsynlig planlagt
2025-02-11 16:00 | 0 | 0 | 0 | 817.19 | PlannedOutage | 0.7 | P1-ScheduledStop | Elhub=0 sammenhengende 34h (≥ 24h), sannsynlig planlagt
2025-02-11 17:00 | 0 | 0 | 0 | 903.42 | PlannedOutage | 0.7 | P1-ScheduledStop | Elhub=0 sammenhengende 34h (≥ 24h), sannsynlig planlagt
2025-02-11 18:00 | 0 | 0 | 0 | 731.53 | PlannedOutage | 0.7 | P1-ScheduledStop | Elhub=0 sammenhengende 34h (≥ 24h), sannsynlig planlagt
2025-02-11 19:00 | 0 | 0 | 0 | 672.15 | PlannedOutage | 0.7 | P1-ScheduledStop | Elhub=0 sammenhengende 34h (≥ 24h), sannsynlig planlagt
2025-02-11 20:00 | 0 | 0 | 0 | 666.25 | PlannedOutage | 0.7 | P1-ScheduledStop | Elhub=0 sammenhengende 34h (≥ 24h), sannsynlig planlagt
2025-02-11 21:00 | 0 | 0 | 0 | 652.71 | PlannedOutage | 0.7 | P1-ScheduledStop | Elhub=0 sammenhengende 34h (≥ 24h), sannsynlig planlagt
2025-02-11 22:00 | 0 | 0 | 0 | 645.42 | PlannedOutage | 0.7 | P1-ScheduledStop | Elhub=0 sammenhengende 34h (≥ 24h), sannsynlig planlagt
2025-02-11 23:00 | 0 | 0 | 0 | 685.61 | PlannedOutage | 0.7 | P1-ScheduledStop | Elhub=0 sammenhengende 34h (≥ 24h), sannsynlig planlagt
2025-02-12 | 0 | 0 | 0 | 678.89 | PlannedOutage | 0.7 | P1-ScheduledStop | Elhub=0 sammenhengende 34h (≥ 24h), sannsynlig planlagt
2025-02-12 01:00 | 0 | 0 | 0 | 674.95 | PlannedOutage | 0.7 | P1-ScheduledStop | Elhub=0 sammenhengende 34h (≥ 24h), sannsynlig planlagt
2025-02-12 02:00 | 0.001504 | 0 | 0 | 670.43 | InService | 0.8 | 0-Normal | Elhub=0.002 (ingen plan-sammenligning)
2025-02-12 03:00 | 1.3995 | 0 | 1.4 | 671.71 | InService | 0.8 | 0-Normal | Elhub=1.399 (ingen plan-sammenligning)
2025-02-12 04:00 | 1.4301 | 0 | 1.4 | 688.74 | InService | 0.8 | 0-Normal | Elhub=1.430 (ingen plan-sammenligning)
2025-02-12 05:00 | 1.4271 | 0 | 1.4 | 1001.3 | InService | 0.8 | 0-Normal | Elhub=1.427 (ingen plan-sammenligning)
2025-02-12 06:00 | 1.4263 | 0 | 1.4 | 1586.12 | InService | 0.8 | 0-Normal | Elhub=1.426 (ingen plan-sammenligning)
2025-02-12 07:00 | 2.0192 | 1.395 | 2 | 1768.13 | InService | 0.95 | 0-Normal | Elhub=2.019 ≈ Plan=1.395 (ratio=145%)
2025-02-12 08:00 | 2.0419 | 1.381 | 2 | 1690.97 | InService | 0.95 | 0-Normal | Elhub=2.042 ≈ Plan=1.381 (ratio=148%)
2025-02-12 09:00 | 1.8447 | 1.965 | 1.8 | 1332.52 | InService | 0.95 | 0-Normal | Elhub=1.845 ≈ Plan=1.965 (ratio=94%)
2025-02-12 10:00 | 1.6396 | 1.982 | 1.6 | 1171.03 | ForcedDerating | 0.65 | D1-ForcedDerating | Elhub=1.640 = 83% av Plan=1.982 – redusert kapasitet
2025-02-12 11:00 | 0.63148 | 0 | 0 | 1147.51 | InService | 0.8 | 0-Normal | Elhub=0.631 (ingen plan-sammenligning)
2025-02-12 12:00 | 1.8045 | 1.8 | 1.8 | 1210.07 | InService | 0.95 | 0-Normal | Elhub=1.804 ≈ Plan=1.800 (ratio=100%)
2025-02-12 13:00 | 1.8357 | 1.8 | 1.8 | 1360.21 | InService | 0.95 | 0-Normal | Elhub=1.836 ≈ Plan=1.800 (ratio=102%)
2025-02-12 14:00 | 1.9341 | 1.9 | 1.9 | 1446.41 | InService | 0.95 | 0-Normal | Elhub=1.934 ≈ Plan=1.900 (ratio=102%)
2025-02-12 15:00 | 2.1891 | 2.2 | 2.2 | 1867.29 | InService | 0.95 | 0-Normal | Elhub=2.189 ≈ Plan=2.200 (ratio=100%)
2025-02-12 16:00 | 2.1975 | 2.2 | 2.2 | 2057.99 | InService | 0.95 | 0-Normal | Elhub=2.197 ≈ Plan=2.200 (ratio=100%)
2025-02-12 17:00 | 2.1967 | 2.2 | 2.2 | 2138.5 | InService | 0.95 | 0-Normal | Elhub=2.197 ≈ Plan=2.200 (ratio=100%)
2025-02-12 18:00 | 2.1956 | 2.2 | 2.2 | 2134.56 | InService | 0.95 | 0-Normal | Elhub=2.196 ≈ Plan=2.200 (ratio=100%)
2025-02-12 19:00 | 0.65888 | 0.6 | 0.6 | 1889.42 | InService | 0.95 | 0-Normal | Elhub=0.659 ≈ Plan=0.600 (ratio=110%)
2025-02-12 20:00 | 0.61772 | 0.6 | 0.6 | 1692.94 | InService | 0.95 | 0-Normal | Elhub=0.618 ≈ Plan=0.600 (ratio=103%)
2025-02-12 21:00 | 0.61776 | 0.6 | 0.6 | 1613 | InService | 0.95 | 0-Normal | Elhub=0.618 ≈ Plan=0.600 (ratio=103%)
2025-02-12 22:00 | 0.61709 | 0.6 | 0.6 | 1034.32 | InService | 0.95 | 0-Normal | Elhub=0.617 ≈ Plan=0.600 (ratio=103%)
2025-02-12 23:00 | 0.004774 | 0 | 0 | 1224.41 | InService | 0.8 | 0-Normal | Elhub=0.005 (ingen plan-sammenligning)
2025-02-13 | 0 | 0 | 0 | 979.48 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=979 ≥ median 778 – uvanlig
2025-02-13 01:00 | 0 | 0 | 0 | 813.24 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=813 ≥ median 778 – uvanlig
2025-02-13 02:00 | 0 | 0 | 0 | 810.44 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=810 ≥ median 778 – uvanlig
2025-02-13 03:00 | 0 | 0 | 0 | 811.26 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=811 ≥ median 778 – uvanlig
2025-02-13 04:00 | 0 | 0 | 0 | 1048.48 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1048 ≥ median 778 – uvanlig
2025-02-13 05:00 | 0 | 0 | 0 | 1463.39 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1463 ≥ median 778 – uvanlig
2025-02-13 06:00 | 0.065952 | 0 | 0 | 2130.23 | InService | 0.8 | 0-Normal | Elhub=0.066 (ingen plan-sammenligning)
2025-02-13 07:00 | 2.1334 | 2.1 | 2.1 | 2347.73 | InService | 0.95 | 0-Normal | Elhub=2.133 ≈ Plan=2.100 (ratio=102%)
2025-02-13 08:00 | 2.143 | 2.1 | 2.1 | 2419.06 | InService | 0.95 | 0-Normal | Elhub=2.143 ≈ Plan=2.100 (ratio=102%)
2025-02-13 09:00 | 2.1413 | 2.1 | 2.1 | 2216.97 | InService | 0.95 | 0-Normal | Elhub=2.141 ≈ Plan=2.100 (ratio=102%)
2025-02-13 10:00 | 0.031848 | 2.1 | 2.1 | 1993.29 | ForcedDerating | 0.65 | D1-ForcedDerating | Elhub=0.032 = 2% av Plan=2.100 – redusert kapasitet
2025-02-13 11:00 | 0 | 0 | 0 | 1883.2 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1883 ≥ median 778 – uvanlig
2025-02-13 12:00 | 0 | 0 | 0 | 1438.52 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1439 ≥ median 778 – uvanlig
2025-02-13 13:00 | 0 | 0 | 0 | 1422.65 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1423 ≥ median 778 – uvanlig
2025-02-13 14:00 | 0.050144 | 0 | 0 | 1457.67 | InService | 0.8 | 0-Normal | Elhub=0.050 (ingen plan-sammenligning)
2025-02-13 15:00 | 1.834 | 1.8 | 1.8 | 1542.78 | InService | 0.95 | 0-Normal | Elhub=1.834 ≈ Plan=1.800 (ratio=102%)
2025-02-13 16:00 | 1.834 | 1.8 | 1.8 | 2057.85 | InService | 0.95 | 0-Normal | Elhub=1.834 ≈ Plan=1.800 (ratio=102%)
2025-02-13 17:00 | 0.63744 | 0.5 | 1.8 | 2163.86 | InService | 0.95 | 0-Normal | Elhub=0.637 ≈ Plan=0.500 (ratio=127%)
2025-02-13 18:00 | 1.7973 | 1.8 | 1.8 | 1928.73 | InService | 0.95 | 0-Normal | Elhub=1.797 ≈ Plan=1.800 (ratio=100%)
2025-02-13 19:00 | 0.02148 | 0 | 0 | 1668.98 | InService | 0.8 | 0-Normal | Elhub=0.021 (ingen plan-sammenligning)
2025-02-13 20:00 | 0 | 0 | 0 | 1482.65 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1483 ≥ median 778 – uvanlig
2025-02-13 21:00 | 0 | 0 | 0 | 1272.51 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1273 ≥ median 778 – uvanlig
2025-02-13 22:00 | 0 | 0 | 0 | 1188.11 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1188 ≥ median 778 – uvanlig
2025-02-13 23:00 | 0 | 0 | 0 | 1448.64 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1449 ≥ median 778 – uvanlig
2025-02-14 | 0 | 0 | 0 | 1384.11 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1384 ≥ median 778 – uvanlig
2025-02-14 01:00 | 0 | 0 | 0 | 1447.35 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1447 ≥ median 778 – uvanlig
2025-02-14 02:00 | 0 | 0 | 0 | 1425.52 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1426 ≥ median 778 – uvanlig
2025-02-14 03:00 | 0 | 0 | 0 | 1193.69 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1194 ≥ median 778 – uvanlig
2025-02-14 04:00 | 0 | 0 | 0 | 1151.1 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1151 ≥ median 778 – uvanlig
2025-02-14 05:00 | 0 | 0 | 0 | 1720.84 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1721 ≥ median 778 – uvanlig
2025-02-14 06:00 | 0.010976 | 0 | 0 | 2429.96 | InService | 0.8 | 0-Normal | Elhub=0.011 (ingen plan-sammenligning)
2025-02-14 07:00 | 2.1178 | 2.1 | 2.1 | 2897.98 | InService | 0.95 | 0-Normal | Elhub=2.118 ≈ Plan=2.100 (ratio=101%)
2025-02-14 08:00 | 2.1445 | 2.1 | 2.1 | 2437.59 | InService | 0.95 | 0-Normal | Elhub=2.144 ≈ Plan=2.100 (ratio=102%)
2025-02-14 09:00 | 2.1425 | 2.1 | 2.1 | 2057.33 | InService | 0.95 | 0-Normal | Elhub=2.142 ≈ Plan=2.100 (ratio=102%)
2025-02-14 10:00 | 2.0409 | 2 | 2 | 1852.83 | InService | 0.95 | 0-Normal | Elhub=2.041 ≈ Plan=2.000 (ratio=102%)
2025-02-14 11:00 | 0.030468 | 0 | 0 | 1703.59 | InService | 0.8 | 0-Normal | Elhub=0.030 (ingen plan-sammenligning)
2025-02-14 12:00 | 0 | 0 | 0 | 1690.68 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1691 ≥ median 778 – uvanlig
2025-02-14 13:00 | 0 | 0 | 0 | 1689.04 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1689 ≥ median 778 – uvanlig
2025-02-14 14:00 | 0.098848 | 0 | 0 | 1573.94 | InService | 0.8 | 0-Normal | Elhub=0.099 (ingen plan-sammenligning)
2025-02-14 15:00 | 2.1366 | 2.1 | 2.1 | 2006.41 | InService | 0.95 | 0-Normal | Elhub=2.137 ≈ Plan=2.100 (ratio=102%)
2025-02-14 16:00 | 0.65072 | 0.5 | 2.1 | 2901.03 | InService | 0.95 | 0-Normal | Elhub=0.651 ≈ Plan=0.500 (ratio=130%)
2025-02-14 17:00 | 0.60231 | 0.5 | 2.1 | 2694.06 | InService | 0.95 | 0-Normal | Elhub=0.602 ≈ Plan=0.500 (ratio=120%)
2025-02-14 18:00 | 2.0895 | 2.1 | 2.1 | 2167.62 | InService | 0.95 | 0-Normal | Elhub=2.090 ≈ Plan=2.100 (ratio=100%)
2025-02-14 19:00 | 0.034918 | 0 | 0 | 1763.78 | InService | 0.8 | 0-Normal | Elhub=0.035 (ingen plan-sammenligning)
2025-02-14 20:00 | 0 | 0 | 0 | 1574.18 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1574 ≥ median 778 – uvanlig
2025-02-14 21:00 | 0 | 0 | 0 | 1416.14 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1416 ≥ median 778 – uvanlig
2025-02-14 22:00 | 0 | 0 | 0 | 1053.83 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1054 ≥ median 778 – uvanlig
2025-02-14 23:00 | 0 | 0 | 0 | 1463.99 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1464 ≥ median 778 – uvanlig
2025-02-15 | 0 | 0 | 0 | 1409.43 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1409 ≥ median 778 – uvanlig
2025-02-15 01:00 | 0 | 0 | 0 | 1221.86 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1222 ≥ median 778 – uvanlig
2025-02-15 02:00 | 0 | 0 | 0 | 1195.28 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1195 ≥ median 778 – uvanlig
2025-02-15 03:00 | 0 | 0 | 0 | 1269.89 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1270 ≥ median 778 – uvanlig
2025-02-15 04:00 | 0 | 0 | 0 | 1299.03 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1299 ≥ median 778 – uvanlig
2025-02-15 05:00 | 0 | 0 | 0 | 1263.24 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1263 ≥ median 778 – uvanlig
2025-02-15 06:00 | 0 | 0 | 0 | 1445.69 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1446 ≥ median 778 – uvanlig
2025-02-15 07:00 | 0 | 0 | 0 | 1490.69 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1491 ≥ median 778 – uvanlig
2025-02-15 08:00 | 0 | 0 | 0 | 1354.64 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1355 ≥ median 778 – uvanlig
2025-02-15 09:00 | 0 | 0 | 0 | 1234.68 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1235 ≥ median 778 – uvanlig
2025-02-15 10:00 | 0 | 0 | 0 | 1139.09 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1139 ≥ median 778 – uvanlig
2025-02-15 11:00 | 0 | 0 | 0 | 1047.22 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1047 ≥ median 778 – uvanlig
2025-02-15 12:00 | 0 | 0 | 0 | 1007.94 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1008 ≥ median 778 – uvanlig
2025-02-15 13:00 | 0 | 0 | 0 | 983.22 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=983 ≥ median 778 – uvanlig
2025-02-15 14:00 | 0 | 0 | 0 | 1125.68 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1126 ≥ median 778 – uvanlig
2025-02-15 15:00 | 0 | 0 | 0 | 1130.93 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1131 ≥ median 778 – uvanlig
2025-02-15 16:00 | 0.76995 | 1.1 | 1.1 | 1514.35 | ForcedDerating | 0.65 | D1-ForcedDerating | Elhub=0.770 = 70% av Plan=1.100 – redusert kapasitet
2025-02-15 17:00 | 1.1232 | 1.1 | 1.1 | 1683.86 | InService | 0.95 | 0-Normal | Elhub=1.123 ≈ Plan=1.100 (ratio=102%)
2025-02-15 18:00 | 1.122 | 1.1 | 1.1 | 1583.6 | InService | 0.95 | 0-Normal | Elhub=1.122 ≈ Plan=1.100 (ratio=102%)
2025-02-15 19:00 | 0.012392 | 0 | 0 | 1411.3 | InService | 0.8 | 0-Normal | Elhub=0.012 (ingen plan-sammenligning)
2025-02-15 20:00 | 0 | 0 | 0 | 1209.85 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1210 ≥ median 778 – uvanlig
2025-02-15 21:00 | 0 | 0 | 0 | 1111.81 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1112 ≥ median 778 – uvanlig
2025-02-15 22:00 | 0 | 0 | 0 | 1063.08 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1063 ≥ median 778 – uvanlig
2025-02-15 23:00 | 0 | 0 | 0 | 1234.83 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1235 ≥ median 778 – uvanlig
2025-02-16 | 0 | 0 | 0 | 1218.27 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1218 ≥ median 778 – uvanlig
2025-02-16 01:00 | 0 | 0 | 0 | 1176.06 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1176 ≥ median 778 – uvanlig
2025-02-16 02:00 | 0 | 0 | 0 | 1141.19 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1141 ≥ median 778 – uvanlig
2025-02-16 03:00 | 0 | 0 | 0 | 1138.16 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1138 ≥ median 778 – uvanlig
2025-02-16 04:00 | 0 | 0 | 0 | 1281.71 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1282 ≥ median 778 – uvanlig
2025-02-16 05:00 | 0 | 0 | 0 | 1275.41 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1275 ≥ median 778 – uvanlig
2025-02-16 06:00 | 0 | 0 | 0 | 1439.14 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1439 ≥ median 778 – uvanlig
2025-02-16 07:00 | 0 | 0 | 0 | 1461.18 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1461 ≥ median 778 – uvanlig
2025-02-16 08:00 | 0 | 0 | 0 | 1470.51 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1471 ≥ median 778 – uvanlig
2025-02-16 09:00 | 0 | 0 | 0 | 1437.16 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1437 ≥ median 778 – uvanlig
2025-02-16 10:00 | 0 | 0 | 0 | 1395.76 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1396 ≥ median 778 – uvanlig
2025-02-16 11:00 | 0 | 0 | 0 | 1409.06 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1409 ≥ median 778 – uvanlig
2025-02-16 12:00 | 0 | 0 | 0 | 1331.39 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1331 ≥ median 778 – uvanlig
2025-02-16 13:00 | 0 | 0 | 0 | 1321.71 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1322 ≥ median 778 – uvanlig
2025-02-16 14:00 | 0.016352 | 0 | 0 | 1457.92 | InService | 0.8 | 0-Normal | Elhub=0.016 (ingen plan-sammenligning)
2025-02-16 15:00 | 1.3172 | 1.3 | 1.3 | 1491.27 | InService | 0.95 | 0-Normal | Elhub=1.317 ≈ Plan=1.300 (ratio=101%)
2025-02-16 16:00 | 1.3267 | 1.3 | 1.3 | 1670.97 | InService | 0.95 | 0-Normal | Elhub=1.327 ≈ Plan=1.300 (ratio=102%)
2025-02-16 17:00 | 0.015168 | 0 | 1.3 | 1872.48 | InService | 0.8 | 0-Normal | Elhub=0.015 (ingen plan-sammenligning)
2025-02-16 18:00 | 0 | 1.3 | 1.3 | 1811.03 | ForcedOutage | 0.8 | U1-UnplannedStop | Plan=1.300 men Elhub=0 (uvarslet stans)
2025-02-16 19:00 | 0 | 0 | 0 | 1729.4 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1729 ≥ median 778 – uvanlig
2025-02-16 20:00 | 0 | 0 | 0 | 1567.77 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1568 ≥ median 778 – uvanlig
2025-02-16 21:00 | 0 | 0 | 0 | 1548.64 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1549 ≥ median 778 – uvanlig
2025-02-16 22:00 | 0 | 0 | 0 | 1435.99 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1436 ≥ median 778 – uvanlig
2025-02-16 23:00 | 0 | 1.287 | 0 | 1218.16 | ForcedOutage | 0.8 | U1-UnplannedStop | Plan=1.287 men Elhub=0 (uvarslet stans)
2025-02-17 | 0 | 1.287 | 0 | 1219.09 | ForcedOutage | 0.8 | U1-UnplannedStop | Plan=1.287 men Elhub=0 (uvarslet stans)
2025-02-17 01:00 | 0 | 1.274 | 0 | 1281.6 | ForcedOutage | 0.8 | U1-UnplannedStop | Plan=1.274 men Elhub=0 (uvarslet stans)
2025-02-17 02:00 | 0 | 1.261 | 0 | 1311.1 | ForcedOutage | 0.8 | U1-UnplannedStop | Plan=1.261 men Elhub=0 (uvarslet stans)
2025-02-17 03:00 | 0 | 1.248 | 0 | 1251.16 | ForcedOutage | 0.8 | U1-UnplannedStop | Plan=1.248 men Elhub=0 (uvarslet stans)
2025-02-17 04:00 | 0 | 1.236 | 0 | 1154.14 | ForcedOutage | 0.8 | U1-UnplannedStop | Plan=1.236 men Elhub=0 (uvarslet stans)
2025-02-17 05:00 | 0 | 1.224 | 0 | 1159.27 | ForcedOutage | 0.8 | U1-UnplannedStop | Plan=1.224 men Elhub=0 (uvarslet stans)
2025-02-17 06:00 | 0.041728 | 1.212 | 0 | 1951.78 | ForcedDerating | 0.65 | D1-ForcedDerating | Elhub=0.042 = 3% av Plan=1.212 – redusert kapasitet
2025-02-17 07:00 | 2.1322 | 0 | 2.1 | 2108.98 | InService | 0.8 | 0-Normal | Elhub=2.132 (ingen plan-sammenligning)
2025-02-17 08:00 | 2.1414 | 0 | 2.1 | 1781.06 | InService | 0.8 | 0-Normal | Elhub=2.141 (ingen plan-sammenligning)
2025-02-17 09:00 | 2.045 | 2.087 | 2 | 1456.98 | InService | 0.95 | 0-Normal | Elhub=2.045 ≈ Plan=2.087 (ratio=98%)
2025-02-17 10:00 | 0.028934 | 2.083 | 1.9 | 1229.35 | ForcedDerating | 0.65 | D1-ForcedDerating | Elhub=0.029 = 1% av Plan=2.083 – redusert kapasitet
2025-02-17 11:00 | 0 | 1.973 | 0 | 1189 | ForcedOutage | 0.8 | U1-UnplannedStop | Plan=1.973 men Elhub=0 (uvarslet stans)
2025-02-17 12:00 | 0 | 1.986 | 0 | 1156.23 | ForcedOutage | 0.8 | U1-UnplannedStop | Plan=1.986 men Elhub=0 (uvarslet stans)
2025-02-17 13:00 | 0 | 1.986 | 0 | 1188.19 | ForcedOutage | 0.8 | U1-UnplannedStop | Plan=1.986 men Elhub=0 (uvarslet stans)
2025-02-17 14:00 | 0.004576 | 0 | 0 | 1140.72 | InService | 0.8 | 0-Normal | Elhub=0.005 (ingen plan-sammenligning)
2025-02-17 15:00 | 1.8105 | 1.8 | 1.8 | 1136.41 | InService | 0.95 | 0-Normal | Elhub=1.811 ≈ Plan=1.800 (ratio=101%)
2025-02-17 16:00 | 2.0325 | 2 | 2 | 1324.16 | InService | 0.95 | 0-Normal | Elhub=2.032 ≈ Plan=2.000 (ratio=102%)
2025-02-17 17:00 | 2.1377 | 2.1 | 2.1 | 1718.43 | InService | 0.95 | 0-Normal | Elhub=2.138 ≈ Plan=2.100 (ratio=102%)
2025-02-17 18:00 | 2.047 | 2 | 2 | 1590.74 | InService | 0.95 | 0-Normal | Elhub=2.047 ≈ Plan=2.000 (ratio=102%)
2025-02-17 19:00 | 0.027328 | 0 | 0 | 1465.03 | InService | 0.8 | 0-Normal | Elhub=0.027 (ingen plan-sammenligning)
2025-02-17 20:00 | 0 | 0 | 0 | 1355.76 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1356 ≥ median 778 – uvanlig
2025-02-17 21:00 | 0 | 0 | 0 | 1256.29 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1256 ≥ median 778 – uvanlig
2025-02-17 22:00 | 0 | 0 | 0 | 1297.34 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1297 ≥ median 778 – uvanlig
2025-02-17 23:00 | 0 | 0 | 0 | 1485.41 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1485 ≥ median 778 – uvanlig
2025-02-18 | 0 | 1.99 | 0 | 1219.65 | ForcedOutage | 0.8 | U1-UnplannedStop | Plan=1.990 men Elhub=0 (uvarslet stans)
2025-02-18 01:00 | 0 | 1.97 | 0 | 1166.05 | ForcedOutage | 0.8 | U1-UnplannedStop | Plan=1.970 men Elhub=0 (uvarslet stans)
2025-02-18 02:00 | 0 | 1.95 | 0 | 1305.52 | ForcedOutage | 0.8 | U1-UnplannedStop | Plan=1.950 men Elhub=0 (uvarslet stans)
2025-02-18 03:00 | 0 | 1.931 | 0 | 1204.5 | ForcedOutage | 0.8 | U1-UnplannedStop | Plan=1.931 men Elhub=0 (uvarslet stans)
2025-02-18 04:00 | 0 | 1.912 | 0 | 1360.86 | ForcedOutage | 0.8 | U1-UnplannedStop | Plan=1.912 men Elhub=0 (uvarslet stans)
2025-02-18 05:00 | 0 | 1.893 | 0 | 1373.09 | ForcedOutage | 0.8 | U1-UnplannedStop | Plan=1.893 men Elhub=0 (uvarslet stans)
2025-02-18 06:00 | 0.015296 | 1.874 | 0 | 1895.77 | ForcedDerating | 0.65 | D1-ForcedDerating | Elhub=0.015 = 1% av Plan=1.874 – redusert kapasitet
2025-02-18 07:00 | 1.9236 | 0 | 1.9 | 2262.66 | InService | 0.8 | 0-Normal | Elhub=1.924 (ingen plan-sammenligning)
2025-02-18 08:00 | 1.9388 | 0 | 1.9 | 1628.37 | InService | 0.8 | 0-Normal | Elhub=1.939 (ingen plan-sammenligning)
2025-02-18 09:00 | 1.9388 | 1.881 | 1.9 | 1400.12 | InService | 0.95 | 0-Normal | Elhub=1.939 ≈ Plan=1.881 (ratio=103%)
2025-02-18 10:00 | 1.8464 | 1.866 | 1.8 | 1236.31 | InService | 0.95 | 0-Normal | Elhub=1.846 ≈ Plan=1.866 (ratio=99%)
2025-02-18 11:00 | 0.025568 | 0 | 0 | 1086.47 | InService | 0.8 | 0-Normal | Elhub=0.026 (ingen plan-sammenligning)
2025-02-18 12:00 | 0 | 0 | 0 | 997.92 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=998 ≥ median 778 – uvanlig
2025-02-18 13:00 | 0 | 0 | 0 | 1107.8 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1108 ≥ median 778 – uvanlig
2025-02-18 14:00 | 0 | 0 | 0 | 1239.57 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1240 ≥ median 778 – uvanlig
2025-02-18 15:00 | 0 | 0 | 0 | 1443.93 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1444 ≥ median 778 – uvanlig
2025-02-18 16:00 | 0 | 0 | 0 | 2001.56 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=2002 ≥ median 778 – uvanlig
2025-02-18 17:00 | 0 | 0 | 0 | 1964.39 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1964 ≥ median 778 – uvanlig
2025-02-18 18:00 | 0 | 0 | 0 | 1755.6 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1756 ≥ median 778 – uvanlig
2025-02-18 19:00 | 0 | 0 | 0 | 1606 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1606 ≥ median 778 – uvanlig
2025-02-18 20:00 | 0 | 0 | 0 | 1458.03 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1458 ≥ median 778 – uvanlig
2025-02-18 21:00 | 0 | 0 | 0 | 1373.21 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1373 ≥ median 778 – uvanlig
2025-02-18 22:00 | 0 | 0 | 0 | 1288.85 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1289 ≥ median 778 – uvanlig
2025-02-18 23:00 | 0 | 0 | 0 | 1009.37 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1009 ≥ median 778 – uvanlig
2025-02-19 | 0 | 0 | 0 | 1119.21 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1119 ≥ median 778 – uvanlig
2025-02-19 01:00 | 0 | 0 | 0 | 1122.7 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1123 ≥ median 778 – uvanlig
2025-02-19 02:00 | 0 | 0 | 0 | 1096.7 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1097 ≥ median 778 – uvanlig
2025-02-19 03:00 | 0 | 0 | 0 | 1065.22 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1065 ≥ median 778 – uvanlig
2025-02-19 04:00 | 0 | 0 | 0 | 1071.63 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=1072 ≥ median 778 – uvanlig
2025-02-19 05:00 | 0.000384 | 0 | 0 | 1233 | InService | 0.8 | 0-Normal | Elhub=0.000 (ingen plan-sammenligning)
2025-02-19 06:00 | 1.1901 | 1.2 | 0 | 1746.84 | InService | 0.95 | 0-Normal | Elhub=1.190 ≈ Plan=1.200 (ratio=99%)
2025-02-19 07:00 | 1.227 | 1.2 | 1.2 | 1954.15 | InService | 0.95 | 0-Normal | Elhub=1.227 ≈ Plan=1.200 (ratio=102%)
2025-02-19 08:00 | 1.2214 | 1.2 | 1.2 | 1472.96 | InService | 0.95 | 0-Normal | Elhub=1.221 ≈ Plan=1.200 (ratio=102%)
2025-02-19 09:00 | 0.01504 | 0 | 1.2 | 1235.22 | InService | 0.8 | 0-Normal | Elhub=0.015 (ingen plan-sammenligning)
2025-02-19 10:00 | 0 | 0 | 1.2 | 1016.25 | PlannedOutage | 0.7 | P1-ScheduledStop | Elhub=0 sammenhengende 40h (≥ 24h), sannsynlig planlagt
2025-02-19 11:00 | 0 | 0 | 0 | 927.64 | PlannedOutage | 0.7 | P1-ScheduledStop | Elhub=0 sammenhengende 40h (≥ 24h), sannsynlig planlagt
2025-02-19 12:00 | 0 | 0 | 0 | 942.21 | PlannedOutage | 0.7 | P1-ScheduledStop | Elhub=0 sammenhengende 40h (≥ 24h), sannsynlig planlagt
2025-02-19 13:00 | 0 | 0 | 0 | 970.78 | PlannedOutage | 0.7 | P1-ScheduledStop | Elhub=0 sammenhengende 40h (≥ 24h), sannsynlig planlagt
2025-02-19 14:00 | 0 | 0 | 0 | 1116.87 | PlannedOutage | 0.7 | P1-ScheduledStop | Elhub=0 sammenhengende 40h (≥ 24h), sannsynlig planlagt
2025-02-19 15:00 | 0 | 0 | 0 | 1101.95 | PlannedOutage | 0.7 | P1-ScheduledStop | Elhub=0 sammenhengende 40h (≥ 24h), sannsynlig planlagt
2025-02-19 16:00 | 0 | 0 | 0 | 1291.07 | PlannedOutage | 0.7 | P1-ScheduledStop | Elhub=0 sammenhengende 40h (≥ 24h), sannsynlig planlagt
2025-02-19 17:00 | 0 | 0 | 0 | 1431.1 | PlannedOutage | 0.7 | P1-ScheduledStop | Elhub=0 sammenhengende 40h (≥ 24h), sannsynlig planlagt
2025-02-19 18:00 | 0 | 0 | 0 | 1376.3 | PlannedOutage | 0.7 | P1-ScheduledStop | Elhub=0 sammenhengende 40h (≥ 24h), sannsynlig planlagt
2025-02-19 19:00 | 0 | 0 | 0 | 1153.6 | PlannedOutage | 0.7 | P1-ScheduledStop | Elhub=0 sammenhengende 40h (≥ 24h), sannsynlig planlagt
2025-02-19 20:00 | 0 | 0 | 0 | 966.81 | PlannedOutage | 0.7 | P1-ScheduledStop | Elhub=0 sammenhengende 40h (≥ 24h), sannsynlig planlagt
2025-02-19 21:00 | 0 | 0 | 0 | 877.97 | PlannedOutage | 0.7 | P1-ScheduledStop | Elhub=0 sammenhengende 40h (≥ 24h), sannsynlig planlagt
2025-02-19 22:00 | 0 | 0 | 0 | 846.49 | PlannedOutage | 0.7 | P1-ScheduledStop | Elhub=0 sammenhengende 40h (≥ 24h), sannsynlig planlagt
2025-02-19 23:00 | 0 | 0 | 0 | 731.86 | PlannedOutage | 0.7 | P1-ScheduledStop | Elhub=0 sammenhengende 40h (≥ 24h), sannsynlig planlagt
2025-02-20 | 0 | 0 | 0 | 709.3 | PlannedOutage | 0.7 | P1-ScheduledStop | Elhub=0 sammenhengende 40h (≥ 24h), sannsynlig planlagt
2025-02-20 01:00 | 0 | 0 | 0 | 702.43 | PlannedOutage | 0.7 | P1-ScheduledStop | Elhub=0 sammenhengende 40h (≥ 24h), sannsynlig planlagt
2025-02-20 02:00 | 0 | 0 | 0 | 688.36 | PlannedOutage | 0.7 | P1-ScheduledStop | Elhub=0 sammenhengende 40h (≥ 24h), sannsynlig planlagt
2025-02-20 03:00 | 0 | 0 | 0 | 678.24 | PlannedOutage | 0.7 | P1-ScheduledStop | Elhub=0 sammenhengende 40h (≥ 24h), sannsynlig planlagt
2025-02-20 04:00 | 0 | 0 | 0 | 681.84 | PlannedOutage | 0.7 | P1-ScheduledStop | Elhub=0 sammenhengende 40h (≥ 24h), sannsynlig planlagt
2025-02-20 05:00 | 0 | 0 | 0 | 740.93 | PlannedOutage | 0.7 | P1-ScheduledStop | Elhub=0 sammenhengende 40h (≥ 24h), sannsynlig planlagt
2025-02-20 06:00 | 0 | 0 | 0 | 1051.85 | PlannedOutage | 0.7 | P1-ScheduledStop | Elhub=0 sammenhengende 40h (≥ 24h), sannsynlig planlagt
2025-02-20 07:00 | 0 | 0 | 0 | 1091.98 | PlannedOutage | 0.7 | P1-ScheduledStop | Elhub=0 sammenhengende 40h (≥ 24h), sannsynlig planlagt
2025-02-20 08:00 | 0 | 0 | 0 | 761.17 | PlannedOutage | 0.7 | P1-ScheduledStop | Elhub=0 sammenhengende 40h (≥ 24h), sannsynlig planlagt
2025-02-20 09:00 | 0 | 0 | 0 | 743.38 | PlannedOutage | 0.7 | P1-ScheduledStop | Elhub=0 sammenhengende 40h (≥ 24h), sannsynlig planlagt
2025-02-20 10:00 | 0 | 0 | 0 | 725.7 | PlannedOutage | 0.7 | P1-ScheduledStop | Elhub=0 sammenhengende 40h (≥ 24h), sannsynlig planlagt
2025-02-20 11:00 | 0 | 0 | 0 | 702.55 | PlannedOutage | 0.7 | P1-ScheduledStop | Elhub=0 sammenhengende 40h (≥ 24h), sannsynlig planlagt
2025-02-20 12:00 | 0 | 0 | 0 | 697.55 | PlannedOutage | 0.7 | P1-ScheduledStop | Elhub=0 sammenhengende 40h (≥ 24h), sannsynlig planlagt
2025-02-20 13:00 | 0 | 0 | 0 | 699.18 | PlannedOutage | 0.7 | P1-ScheduledStop | Elhub=0 sammenhengende 40h (≥ 24h), sannsynlig planlagt
2025-02-20 14:00 | 0 | 0 | 0 | 729.42 | PlannedOutage | 0.7 | P1-ScheduledStop | Elhub=0 sammenhengende 40h (≥ 24h), sannsynlig planlagt
2025-02-20 15:00 | 0 | 0 | 0 | 715.93 | PlannedOutage | 0.7 | P1-ScheduledStop | Elhub=0 sammenhengende 40h (≥ 24h), sannsynlig planlagt
2025-02-20 16:00 | 0 | 0 | 0 | 713.37 | PlannedOutage | 0.7 | P1-ScheduledStop | Elhub=0 sammenhengende 40h (≥ 24h), sannsynlig planlagt
2025-02-20 17:00 | 0 | 0 | 0 | 698.94 | PlannedOutage | 0.7 | P1-ScheduledStop | Elhub=0 sammenhengende 40h (≥ 24h), sannsynlig planlagt
2025-02-20 18:00 | 0 | 0 | 0 | 663.58 | PlannedOutage | 0.7 | P1-ScheduledStop | Elhub=0 sammenhengende 40h (≥ 24h), sannsynlig planlagt
2025-02-20 19:00 | 0 | 0 | 0 | 629.27 | PlannedOutage | 0.7 | P1-ScheduledStop | Elhub=0 sammenhengende 40h (≥ 24h), sannsynlig planlagt
2025-02-20 20:00 | 0 | 0 | 0 | 604.03 | PlannedOutage | 0.7 | P1-ScheduledStop | Elhub=0 sammenhengende 40h (≥ 24h), sannsynlig planlagt
2025-02-20 21:00 | 0 | 0 | 0 | 589.84 | PlannedOutage | 0.7 | P1-ScheduledStop | Elhub=0 sammenhengende 40h (≥ 24h), sannsynlig planlagt
2025-02-20 22:00 | 0 | 0 | 0 | 582.74 | PlannedOutage | 0.7 | P1-ScheduledStop | Elhub=0 sammenhengende 40h (≥ 24h), sannsynlig planlagt
2025-02-20 23:00 | 0 | 0 | 0 | 563.88 | PlannedOutage | 0.7 | P1-ScheduledStop | Elhub=0 sammenhengende 40h (≥ 24h), sannsynlig planlagt
2025-02-21 | 0 | 0 | 0 | 571.54 | PlannedOutage | 0.7 | P1-ScheduledStop | Elhub=0 sammenhengende 40h (≥ 24h), sannsynlig planlagt
2025-02-21 01:00 | 0 | 0 | 0 | 567.94 | PlannedOutage | 0.7 | P1-ScheduledStop | Elhub=0 sammenhengende 40h (≥ 24h), sannsynlig planlagt
2025-02-21 02:00 | 0.019392 | 0.215 | 0 | 563.76 | ForcedDerating | 0.65 | D1-ForcedDerating | Elhub=0.019 = 9% av Plan=0.215 – redusert kapasitet
2025-02-21 03:00 | 1.7144 | 0.215 | 1.7 | 574.79 | InService | 0.95 | 0-Normal | Elhub=1.714 ≈ Plan=0.215 (ratio=797%)
2025-02-21 04:00 | 1.735 | 1.7 | 1.7 | 601.83 | InService | 0.95 | 0-Normal | Elhub=1.735 ≈ Plan=1.700 (ratio=102%)
2025-02-21 05:00 | 1.7369 | 1.7 | 1.7 | 662.08 | InService | 0.95 | 0-Normal | Elhub=1.737 ≈ Plan=1.700 (ratio=102%)
2025-02-21 06:00 | 1.732 | 1.7 | 1.7 | 974.43 | InService | 0.95 | 0-Normal | Elhub=1.732 ≈ Plan=1.700 (ratio=102%)
2025-02-21 07:00 | 1.734 | 2.1 | 2.1 | 1515.32 | ForcedDerating | 0.65 | D1-ForcedDerating | Elhub=1.734 = 83% av Plan=2.100 – redusert kapasitet
2025-02-21 08:00 | 1.7357 | 1.7 | 2.1 | 1160.84 | InService | 0.95 | 0-Normal | Elhub=1.736 ≈ Plan=1.700 (ratio=102%)
2025-02-21 09:00 | 0.022276 | 0 | 2.1 | 907.68 | InService | 0.8 | 0-Normal | Elhub=0.022 (ingen plan-sammenligning)
2025-02-21 10:00 | 0 | 0 | 2.1 | 759.11 | ReserveShutdown | 0.55 | M1-MarketDriven | Elhub=0, Plan=0, Spotpris=759 < median 778 – markedsstyrt
2025-02-21 11:00 | 0 | 0 | 0 | 728.47 | ReserveShutdown | 0.55 | M1-MarketDriven | Elhub=0, Plan=0, Spotpris=728 < median 778 – markedsstyrt
2025-02-21 12:00 | 0 | 0 | 0 | 708.39 | ReserveShutdown | 0.55 | M1-MarketDriven | Elhub=0, Plan=0, Spotpris=708 < median 778 – markedsstyrt
2025-02-21 13:00 | 0 | 0 | 0 | 708.16 | ReserveShutdown | 0.55 | M1-MarketDriven | Elhub=0, Plan=0, Spotpris=708 < median 778 – markedsstyrt
2025-02-21 14:00 | 0 | 0 | 0 | 745.3 | ReserveShutdown | 0.55 | M1-MarketDriven | Elhub=0, Plan=0, Spotpris=745 < median 778 – markedsstyrt
2025-02-21 15:00 | 0 | 0 | 1.8 | 783.49 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=783 ≥ median 778 – uvanlig
2025-02-21 16:00 | 0 | 0 | 1.8 | 825.74 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=826 ≥ median 778 – uvanlig
2025-02-21 17:00 | 0 | 0 | 1.8 | 790.22 | ForcedOutage | 0.45 | U2-UnexpectedStop | Elhub=0, Plan=0, Spotpris=790 ≥ median 778 – uvanlig
2025-02-21 18:00 | 0 | 0 | 0.6 | 656.85 | ReserveShutdown | 0.55 | M1-MarketDriven | Elhub=0, Plan=0, Spotpris=657 < median 778 – markedsstyrt
2025-02-21 19:00 | 0 | 0 | 0 | 612.51 | ReserveShutdown | 0.55 | M1-MarketDriven | Elhub=0, Plan=0, Spotpris=613 < median 778 – markedsstyrt
2025-02-21 20:00 | 0 | 0 | 0 | 586.74 | ReserveShutdown | 0.55 | M1-MarketDriven | Elhub=0, Plan=0, Spotpris=587 < median 778 – markedsstyrt
2025-02-21 21:00 | 0 | 0 | 0 | 563.65 | ReserveShutdown | 0.55 | M1-MarketDriven | Elhub=0, Plan=0, Spotpris=564 < median 778 – markedsstyrt
2025-02-21 22:00 | 0 | 0 | 0 | 551.23 | ReserveShutdown | 0.55 | M1-MarketDriven | Elhub=0, Plan=0, Spotpris=551 < median 778 – markedsstyrt
2025-02-21 23:00 | 0 | 0 | 0 | 557.16 | ReserveShutdown | 0.55 | M1-MarketDriven | Elhub=0, Plan=0, Spotpris=557 < median 778 – markedsstyrt
2025-02-22 | 0 | 0 | 0 | 545.77 | ReserveShutdown | 0.55 | M1-MarketDriven | Elhub=0, Plan=0, Spotpris=546 < median 778 – markedsstyrt
2025-02-22 01:00 | 0 | 0 | 0 | 527.51 | ReserveShutdown | 0.55 | M1-MarketDriven | Elhub=0, Plan=0, Spotpris=528 < median 778 – markedsstyrt
2025-02-22 02:00 | 0 | 0 | 0 | 475.42 | ReserveShutdown | 0.55 | M1-MarketDriven | Elhub=0, Plan=0, Spotpris=475 < median 778 – markedsstyrt
2025-02-22 03:00 | 0 | 0 | 0 | 463.91 | ReserveShutdown | 0.55 | M1-MarketDriven | Elhub=0, Plan=0, Spotpris=464 < median 778 – markedsstyrt
2025-02-22 04:00 | 0 | 0 | 0 | 536 | ReserveShutdown | 0.55 | M1-MarketDriven | Elhub=0, Plan=0, Spotpris=536 < median 778 – markedsstyrt
2025-02-22 05:00 | 0 | 0 | 0 | 553.21 | ReserveShutdown | 0.55 | M1-MarketDriven | Elhub=0, Plan=0, Spotpris=553 < median 778 – markedsstyrt
2025-02-22 06:00 | 0 | 0 | 0 | 569.6 | ReserveShutdown | 0.55 | M1-MarketDriven | Elhub=0, Plan=0, Spotpris=570 < median 778 – markedsstyrt
2025-02-22 07:00 | 0 | 0 | 0 | 588.09 | ReserveShutdown | 0.55 | M1-MarketDriven | Elhub=0, Plan=0, Spotpris=588 < median 778 – markedsstyrt
2025-02-22 08:00 | 0 | 0 | 0 | 596.69 | ReserveShutdown | 0.55 | M1-MarketDriven | Elhub=0, Plan=0, Spotpris=597 < median 778 – markedsstyrt
2025-02-22 09:00 | 0.99878 | 0 | 0 | 586.35 | InService | 0.8 | 0-Normal | Elhub=0.999 (ingen plan-sammenligning)
2025-02-22 10:00 | 2.1368 | 2.1 | 0 | 556.58 | InService | 0.95 | 0-Normal | Elhub=2.137 ≈ Plan=2.100 (ratio=102%)
2025-02-22 11:00 | 2.186 | 2.1 | 0 | 554.37 | InService | 0.95 | 0-Normal | Elhub=2.186 ≈ Plan=2.100 (ratio=104%)
2025-02-22 12:00 | 2.1898 | 2.1 | 0 | 582.97 | InService | 0.95 | 0-Normal | Elhub=2.190 ≈ Plan=2.100 (ratio=104%)
2025-02-22 13:00 | 2.1911 | 2.1 | 0 | 595.18 | InService | 0.95 | 0-Normal | Elhub=2.191 ≈ Plan=2.100 (ratio=104%)
2025-02-22 14:00 | 2.1911 | 2.1 | 0 | 598.55 | InService | 0.95 | 0-Normal | Elhub=2.191 ≈ Plan=2.100 (ratio=104%)
2025-02-22 15:00 | 2.1896 | 2.1 | 1.4 | 613.44 | InService | 0.95 | 0-Normal | Elhub=2.190 ≈ Plan=2.100 (ratio=104%)
2025-02-22 16:00 | 2.1906 | 2.1 | 1.6 | 628.09 | InService | 0.95 | 0-Normal | Elhub=2.191 ≈ Plan=2.100 (ratio=104%)
2025-02-22 17:00 | 2.1888 | 2.1 | 1.6 | 624.02 | InService | 0.95 | 0-Normal | Elhub=2.189 ≈ Plan=2.100 (ratio=104%)
2025-02-22 18:00 | 2.1889 | 2.1 | 1.4 | 613.09 | InService | 0.95 | 0-Normal | Elhub=2.189 ≈ Plan=2.100 (ratio=104%)
2025-02-22 19:00 | 2.1875 | 2.1 | 0 | 599.83 | InService | 0.95 | 0-Normal | Elhub=2.187 ≈ Plan=2.100 (ratio=104%)
2025-02-22 20:00 | 2.1898 | 2.1 | 0 | 596.23 | InService | 0.95 | 0-Normal | Elhub=2.190 ≈ Plan=2.100 (ratio=104%)
2025-02-22 21:00 | 2.189 | 2.1 | 0 | 594.02 | InService | 0.95 | 0-Normal | Elhub=2.189 ≈ Plan=2.100 (ratio=104%)
2025-02-22 22:00 | 2.1886 | 2.1 | 0 | 591.35 | InService | 0.95 | 0-Normal | Elhub=2.189 ≈ Plan=2.100 (ratio=104%)
2025-02-22 23:00 | 2.1893 | 2.1 | 2.1 | 568.58 | InService | 0.95 | 0-Normal | Elhub=2.189 ≈ Plan=2.100 (ratio=104%)
2025-02-23 | 2.1892 | 2.1 | 2.1 | 567.65 | InService | 0.95 | 0-Normal | Elhub=2.189 ≈ Plan=2.100 (ratio=104%)
2025-02-23 01:00 | 2.1888 | 2.1 | 2.1 | 566.71 | InService | 0.95 | 0-Normal | Elhub=2.189 ≈ Plan=2.100 (ratio=104%)
2025-02-23 02:00 | 2.1879 | 2.1 | 2.1 | 566.48 | InService | 0.95 | 0-Normal | Elhub=2.188 ≈ Plan=2.100 (ratio=104%)
2025-02-23 03:00 | 2.1897 | 2.1 | 2.1 | 567.41 | InService | 0.95 | 0-Normal | Elhub=2.190 ≈ Plan=2.100 (ratio=104%)
2025-02-23 04:00 | 2.1901 | 2.1 | 2.1 | 569.74 | InService | 0.95 | 0-Normal | Elhub=2.190 ≈ Plan=2.100 (ratio=104%)
2025-02-23 05:00 | 2.1895 | 2.1 | 2.1 | 577.44 | InService | 0.95 | 0-Normal | Elhub=2.189 ≈ Plan=2.100 (ratio=104%)
2025-02-23 06:00 | 2.19 | 2.1 | 2.1 | 582.34 | InService | 0.95 | 0-Normal | Elhub=2.190 ≈ Plan=2.100 (ratio=104%)
2025-02-23 07:00 | 2.1902 | 2.1 | 2.1 | 592.73 | InService | 0.95 | 0-Normal | Elhub=2.190 ≈ Plan=2.100 (ratio=104%)
2025-02-23 08:00 | 2.1899 | 2.1 | 2.1 | 604.16 | InService | 0.95 | 0-Normal | Elhub=2.190 ≈ Plan=2.100 (ratio=104%)
2025-02-23 09:00 | 2.1904 | 2.1 | 2.1 | 597.86 | InService | 0.95 | 0-Normal | Elhub=2.190 ≈ Plan=2.100 (ratio=104%)
2025-02-23 10:00 | 2.1887 | 2.1 | 2.1 | 590.04 | InService | 0.95 | 0-Normal | Elhub=2.189 ≈ Plan=2.100 (ratio=104%)
2025-02-23 11:00 | 2.189 | 2.1 | 2.1 | 563.1 | InService | 0.95 | 0-Normal | Elhub=2.189 ≈ Plan=2.100 (ratio=104%)
2025-02-23 12:00 | 2.1896 | 2.1 | 2.1 | 553.06 | InService | 0.95 | 0-Normal | Elhub=2.190 ≈ Plan=2.100 (ratio=104%)
2025-02-23 13:00 | 2.1893 | 2.1 | 2.1 | 553.41 | InService | 0.95 | 0-Normal | Elhub=2.189 ≈ Plan=2.100 (ratio=104%)
2025-02-23 14:00 | 2.1898 | 2.1 | 2.1 | 573.24 | InService | 0.95 | 0-Normal | Elhub=2.190 ≈ Plan=2.100 (ratio=104%)
2025-02-23 15:00 | 2.1896 | 2.1 | 2.1 | 596.69 | InService | 0.95 | 0-Normal | Elhub=2.190 ≈ Plan=2.100 (ratio=104%)
2025-02-23 16:00 | 2.1912 | 2.1 | 2.1 | 641.84 | InService | 0.95 | 0-Normal | Elhub=2.191 ≈ Plan=2.100 (ratio=104%)
2025-02-23 17:00 | 2.1892 | 2.1 | 2.1 | 639.85 | InService | 0.95 | 0-Normal | Elhub=2.189 ≈ Plan=2.100 (ratio=104%)
2025-02-23 18:00 | 2.189 | 2.1 | 2.1 | 623.64 | InService | 0.95 | 0-Normal | Elhub=2.189 ≈ Plan=2.100 (ratio=104%)
2025-02-23 19:00 | 2.1883 | 2.1 | 2.1 | 596.46 | InService | 0.95 | 0-Normal | Elhub=2.188 ≈ Plan=2.100 (ratio=104%)
2025-02-23 20:00 | 2.188 | 2.1 | 2.1 | 580.24 | InService | 0.95 | 0-Normal | Elhub=2.188 ≈ Plan=2.100 (ratio=104%)
2025-02-23 21:00 | 2.1865 | 2.1 | 2.1 | 569.63 | InService | 0.95 | 0-Normal | Elhub=2.186 ≈ Plan=2.100 (ratio=104%)
2025-02-23 22:00 | 2.1849 | 2.1 | 2.1 | 552.83 | InService | 0.95 | 0-Normal | Elhub=2.185 ≈ Plan=2.100 (ratio=104%)
2025-02-23 23:00 | 2.1868 | 2.1 | 2.1 | 484.59 | InService | 0.95 | 0-Normal | Elhub=2.187 ≈ Plan=2.100 (ratio=104%)
2025-02-24 | 2.1817 | 2.1 | 2.1 | 435.47 | InService | 0.95 | 0-Normal | Elhub=2.182 ≈ Plan=2.100 (ratio=104%)
2025-02-24 01:00 | 2.1854 | 2.1 | 2.1 | 361.4 | InService | 0.95 | 0-Normal | Elhub=2.185 ≈ Plan=2.100 (ratio=104%)
2025-02-24 02:00 | 2.19 | 2.1 | 2.1 | 313.45 | InService | 0.95 | 0-Normal | Elhub=2.190 ≈ Plan=2.100 (ratio=104%)
2025-02-24 03:00 | 2.1915 | 2.1 | 2.1 | 335.27 | InService | 0.95 | 0-Normal | Elhub=2.192 ≈ Plan=2.100 (ratio=104%)
2025-02-24 04:00 | 2.1948 | 2.1 | 2.1 | 421.71 | InService | 0.95 | 0-Normal | Elhub=2.195 ≈ Plan=2.100 (ratio=105%)
2025-02-24 05:00 | 2.1965 | 2.1 | 2.1 | 442.01 | InService | 0.95 | 0-Normal | Elhub=2.196 ≈ Plan=2.100 (ratio=105%)
2025-02-24 06:00 | 2.1882 | 2.1 | 2.1 | 547.23 | InService | 0.95 | 0-Normal | Elhub=2.188 ≈ Plan=2.100 (ratio=104%)
2025-02-24 07:00 | 2.1806 | 2.1 | 2.1 | 579.89 | InService | 0.95 | 0-Normal | Elhub=2.181 ≈ Plan=2.100 (ratio=104%)
2025-02-24 08:00 | 2.1973 | 2.1 | 2.1 | 574.29 | InService | 0.95 | 0-Normal | Elhub=2.197 ≈ Plan=2.100 (ratio=105%)
2025-02-24 09:00 | 2.1906 | 2.1 | 2.1 | 569.16 | InService | 0.95 | 0-Normal | Elhub=2.191 ≈ Plan=2.100 (ratio=104%)
2025-02-24 10:00 | 2.1926 | 2.1 | 2.1 | 550.85 | InService | 0.95 | 0-Normal | Elhub=2.193 ≈ Plan=2.100 (ratio=104%)
2025-02-24 11:00 | 2.1938 | 2.1 | 2.1 | 558.78 | InService | 0.95 | 0-Normal | Elhub=2.194 ≈ Plan=2.100 (ratio=104%)
2025-02-24 12:00 | 2.1921 | 2.1 | 2.1 | 563.45 | InService | 0.95 | 0-Normal | Elhub=2.192 ≈ Plan=2.100 (ratio=104%)
2025-02-24 13:00 | 0.85475 | 2.1 | 2.1 | 564.73 | ForcedDerating | 0.65 | D1-ForcedDerating | Elhub=0.855 = 41% av Plan=2.100 – redusert kapasitet
2025-02-24 14:00 | 2.0968 | 2.1 | 2.1 | 558.2 | InService | 0.95 | 0-Normal | Elhub=2.097 ≈ Plan=2.100 (ratio=100%)
2025-02-24 15:00 | 2.1985 | 2.1 | 2.1 | 574.64 | InService | 0.95 | 0-Normal | Elhub=2.198 ≈ Plan=2.100 (ratio=105%)
2025-02-24 16:00 | 2.1965 | 2.1 | 2.1 | 587.13 | InService | 0.95 | 0-Normal | Elhub=2.196 ≈ Plan=2.100 (ratio=105%)
2025-02-24 17:00 | 2.1945 | 2.1 | 2.1 | 588.53 | InService | 0.95 | 0-Normal | Elhub=2.195 ≈ Plan=2.100 (ratio=104%)
2025-02-24 18:00 | 2.1938 | 2.1 | 2.1 | 589.11 | InService | 0.95 | 0-Normal | Elhub=2.194 ≈ Plan=2.100 (ratio=104%)
2025-02-24 19:00 | 2.1935 | 2.1 | 2.1 | 588.88 | InService | 0.95 | 0-Normal | Elhub=2.193 ≈ Plan=2.100 (ratio=104%)
2025-02-24 20:00 | 2.1936 | 2.1 | 2.1 | 588.06 | InService | 0.95 | 0-Normal | Elhub=2.194 ≈ Plan=2.100 (ratio=104%)
2025-02-24 21:00 | 2.192 | 2.1 | 2.1 | 585.61 | InService | 0.95 | 0-Normal | Elhub=2.192 ≈ Plan=2.100 (ratio=104%)
2025-02-24 22:00 | 2.1892 | 2.1 | 2.1 | 579.31 | InService | 0.95 | 0-Normal | Elhub=2.189 ≈ Plan=2.100 (ratio=104%)
2025-02-24 23:00 | 2.192 | 2.1 | 2.1 | 580.34 | InService | 0.95 | 0-Normal | Elhub=2.192 ≈ Plan=2.100 (ratio=104%)
2025-02-25 | 2.1915 | 2.1 | 2.1 | 580.92 | InService | 0.95 | 0-Normal | Elhub=2.191 ≈ Plan=2.100 (ratio=104%)
2025-02-25 01:00 | 2.1901 | 2.1 | 2.1 | 584.88 | InService | 0.95 | 0-Normal | Elhub=2.190 ≈ Plan=2.100 (ratio=104%)
2025-02-25 02:00 | 2.1901 | 2.1 | 2.1 | 581.74 | InService | 0.95 | 0-Normal | Elhub=2.190 ≈ Plan=2.100 (ratio=104%)
2025-02-25 03:00 | 2.1887 | 2.1 | 2.1 | 579.65 | InService | 0.95 | 0-Normal | Elhub=2.189 ≈ Plan=2.100 (ratio=104%)
2025-02-25 04:00 | 2.1784 | 2.1 | 2.1 | 572.79 | InService | 0.95 | 0-Normal | Elhub=2.178 ≈ Plan=2.100 (ratio=104%)
2025-02-25 05:00 | 2.1773 | 2.1 | 2.1 | 585.46 | InService | 0.95 | 0-Normal | Elhub=2.177 ≈ Plan=2.100 (ratio=104%)
2025-02-25 06:00 | 2.1773 | 2.1 | 2.1 | 611.38 | InService | 0.95 | 0-Normal | Elhub=2.177 ≈ Plan=2.100 (ratio=104%)
2025-02-25 07:00 | 2.1784 | 2.1 | 2.1 | 625.8 | InService | 0.95 | 0-Normal | Elhub=2.178 ≈ Plan=2.100 (ratio=104%)
2025-02-25 08:00 | 2.1777 | 2.1 | 2.1 | 643.47 | InService | 0.95 | 0-Normal | Elhub=2.178 ≈ Plan=2.100 (ratio=104%)
2025-02-25 09:00 | 2.1768 | 2.1 | 2.1 | 633.36 | InService | 0.95 | 0-Normal | Elhub=2.177 ≈ Plan=2.100 (ratio=104%)
2025-02-25 10:00 | 1.9938 | 2.1 | 2.1 | 620.8 | InService | 0.95 | 0-Normal | Elhub=1.994 ≈ Plan=2.100 (ratio=95%)
2025-02-25 11:00 | 1.666 | 2.1 | 2.1 | 612.08 | ForcedDerating | 0.65 | D1-ForcedDerating | Elhub=1.666 = 79% av Plan=2.100 – redusert kapasitet
2025-02-25 12:00 | 2.1957 | 2.1 | 2.1 | 609.29 | InService | 0.95 | 0-Normal | Elhub=2.196 ≈ Plan=2.100 (ratio=105%)
2025-02-25 13:00 | 2.1918 | 2.1 | 2.1 | 611.85 | InService | 0.95 | 0-Normal | Elhub=2.192 ≈ Plan=2.100 (ratio=104%)
2025-02-25 14:00 | 2.1808 | 2.1 | 2.1 | 622.54 | InService | 0.95 | 0-Normal | Elhub=2.181 ≈ Plan=2.100 (ratio=104%)
2025-02-25 15:00 | 2.1829 | 2.1 | 2.1 | 670.44 | InService | 0.95 | 0-Normal | Elhub=2.183 ≈ Plan=2.100 (ratio=104%)
2025-02-25 16:00 | 2.1818 | 2.1 | 2.1 | 670.56 | InService | 0.95 | 0-Normal | Elhub=2.182 ≈ Plan=2.100 (ratio=104%)
2025-02-25 17:00 | 2.1789 | 2.1 | 2.1 | 669.86 | InService | 0.95 | 0-Normal | Elhub=2.179 ≈ Plan=2.100 (ratio=104%)
2025-02-25 18:00 | 2.1791 | 2.1 | 2.1 | 632.08 | InService | 0.95 | 0-Normal | Elhub=2.179 ≈ Plan=2.100 (ratio=104%)
2025-02-25 19:00 | 2.1775 | 2.1 | 2.1 | 644.17 | InService | 0.95 | 0-Normal | Elhub=2.177 ≈ Plan=2.100 (ratio=104%)
2025-02-25 20:00 | 2.1791 | 2.1 | 2.1 | 611.96 | InService | 0.95 | 0-Normal | Elhub=2.179 ≈ Plan=2.100 (ratio=104%)
2025-02-25 21:00 | 2.1765 | 2.1 | 2.1 | 585.92 | InService | 0.95 | 0-Normal | Elhub=2.176 ≈ Plan=2.100 (ratio=104%)
2025-02-25 22:00 | 2.178 | 2.1 | 2.1 | 571.86 | InService | 0.95 | 0-Normal | Elhub=2.178 ≈ Plan=2.100 (ratio=104%)
2025-02-25 23:00 | 2.1766 | 2.1 | 2.1 | 593.47 | InService | 0.95 | 0-Normal | Elhub=2.177 ≈ Plan=2.100 (ratio=104%)
2025-02-26 | 2.1772 | 2.1 | 2.1 | 593.82 | InService | 0.95 | 0-Normal | Elhub=2.177 ≈ Plan=2.100 (ratio=104%)
2025-02-26 01:00 | 2.1757 | 2.1 | 2.1 | 593.93 | InService | 0.95 | 0-Normal | Elhub=2.176 ≈ Plan=2.100 (ratio=104%)
2025-02-26 02:00 | 2.1776 | 2.1 | 2.1 | 594.05 | InService | 0.95 | 0-Normal | Elhub=2.178 ≈ Plan=2.100 (ratio=104%)
2025-02-26 03:00 | 2.1769 | 2.1 | 2.1 | 594.75 | InService | 0.95 | 0-Normal | Elhub=2.177 ≈ Plan=2.100 (ratio=104%)
2025-02-26 04:00 | 2.1756 | 2.1 | 2.1 | 593.93 | InService | 0.95 | 0-Normal | Elhub=2.176 ≈ Plan=2.100 (ratio=104%)
2025-02-26 05:00 | 2.1751 | 2.1 | 2.1 | 603.62 | InService | 0.95 | 0-Normal | Elhub=2.175 ≈ Plan=2.100 (ratio=104%)
2025-02-26 06:00 | 2.1771 | 2.1 | 2.1 | 749.18 | InService | 0.95 | 0-Normal | Elhub=2.177 ≈ Plan=2.100 (ratio=104%)
2025-02-26 07:00 | 2.1781 | 2.1 | 2.1 | 1049.77 | InService | 0.95 | 0-Normal | Elhub=2.178 ≈ Plan=2.100 (ratio=104%)
2025-02-26 08:00 | 2.1953 | 2.1 | 2.1 | 932.89 | InService | 0.95 | 0-Normal | Elhub=2.195 ≈ Plan=2.100 (ratio=105%)
2025-02-26 09:00 | 2.1956 | 2.1 | 2.1 | 676.87 | InService | 0.95 | 0-Normal | Elhub=2.196 ≈ Plan=2.100 (ratio=105%)
2025-02-26 10:00 | 2.1954 | 2.1 | 2.1 | 696.58 | InService | 0.95 | 0-Normal | Elhub=2.195 ≈ Plan=2.100 (ratio=105%)
2025-02-26 11:00 | 2.1955 | 2.1 | 2.1 | 649.57 | InService | 0.95 | 0-Normal | Elhub=2.195 ≈ Plan=2.100 (ratio=105%)
2025-02-26 12:00 | 2.1947 | 2.1 | 2.1 | 625.78 | InService | 0.95 | 0-Normal | Elhub=2.195 ≈ Plan=2.100 (ratio=105%)
2025-02-26 13:00 | 2.1944 | 2.1 | 2.1 | 620.76 | InService | 0.95 | 0-Normal | Elhub=2.194 ≈ Plan=2.100 (ratio=104%)
2025-02-26 14:00 | 2.1943 | 2.1 | 2.1 | 659.14 | InService | 0.95 | 0-Normal | Elhub=2.194 ≈ Plan=2.100 (ratio=104%)
2025-02-26 15:00 | 2.1933 | 2.1 | 2.1 | 727.49 | InService | 0.95 | 0-Normal | Elhub=2.193 ≈ Plan=2.100 (ratio=104%)
2025-02-26 16:00 | 2.1865 | 2.1 | 2.1 | 1068.08 | InService | 0.95 | 0-Normal | Elhub=2.187 ≈ Plan=2.100 (ratio=104%)
2025-02-26 17:00 | 2.1875 | 2.1 | 2.1 | 1209.45 | InService | 0.95 | 0-Normal | Elhub=2.188 ≈ Plan=2.100 (ratio=104%)
2025-02-26 18:00 | 2.1869 | 2.1 | 2.1 | 786.39 | InService | 0.95 | 0-Normal | Elhub=2.187 ≈ Plan=2.100 (ratio=104%)
2025-02-26 19:00 | 2.1867 | 2.1 | 2.1 | 642.92 | InService | 0.95 | 0-Normal | Elhub=2.187 ≈ Plan=2.100 (ratio=104%)
2025-02-26 20:00 | 2.1869 | 2.1 | 2.1 | 634.99 | InService | 0.95 | 0-Normal | Elhub=2.187 ≈ Plan=2.100 (ratio=104%)
2025-02-26 21:00 | 2.1868 | 2.1 | 2.1 | 615.51 | InService | 0.95 | 0-Normal | Elhub=2.187 ≈ Plan=2.100 (ratio=104%)
2025-02-26 22:00 | 2.1869 | 2.1 | 2.1 | 602.8 | InService | 0.95 | 0-Normal | Elhub=2.187 ≈ Plan=2.100 (ratio=104%)
2025-02-26 23:00 | 2.1863 | 2.1 | 1.4 | 574.15 | InService | 0.95 | 0-Normal | Elhub=2.186 ≈ Plan=2.100 (ratio=104%)
2025-02-27 | 2.1844 | 2.1 | 1.4 | 556.74 | InService | 0.95 | 0-Normal | Elhub=2.184 ≈ Plan=2.100 (ratio=104%)
2025-02-27 01:00 | 2.1857 | 2.1 | 1.4 | 553.35 | InService | 0.95 | 0-Normal | Elhub=2.186 ≈ Plan=2.100 (ratio=104%)
2025-02-27 02:00 | 2.1865 | 2.1 | 1.4 | 550.54 | InService | 0.95 | 0-Normal | Elhub=2.187 ≈ Plan=2.100 (ratio=104%)
2025-02-27 03:00 | 2.1858 | 2.1 | 1.6 | 555.22 | InService | 0.95 | 0-Normal | Elhub=2.186 ≈ Plan=2.100 (ratio=104%)
2025-02-27 04:00 | 2.1855 | 2.1 | 1.6 | 581.51 | InService | 0.95 | 0-Normal | Elhub=2.186 ≈ Plan=2.100 (ratio=104%)
2025-02-27 05:00 | 2.1849 | 2.1 | 1.6 | 641.23 | InService | 0.95 | 0-Normal | Elhub=2.185 ≈ Plan=2.100 (ratio=104%)
2025-02-27 06:00 | 2.1849 | 2.1 | 1.6 | 1625.34 | InService | 0.95 | 0-Normal | Elhub=2.185 ≈ Plan=2.100 (ratio=104%)
2025-02-27 07:00 | 2.185 | 2.1 | 2.1 | 1785.91 | InService | 0.95 | 0-Normal | Elhub=2.185 ≈ Plan=2.100 (ratio=104%)
2025-02-27 08:00 | 2.1867 | 2.1 | 2.1 | 1586.89 | InService | 0.95 | 0-Normal | Elhub=2.187 ≈ Plan=2.100 (ratio=104%)
2025-02-27 09:00 | 2.1847 | 2.1 | 2.1 | 1426.67 | InService | 0.95 | 0-Normal | Elhub=2.185 ≈ Plan=2.100 (ratio=104%)
2025-02-27 10:00 | 2.184 | 2.1 | 2.1 | 1223.68 | InService | 0.95 | 0-Normal | Elhub=2.184 ≈ Plan=2.100 (ratio=104%)
2025-02-27 11:00 | 2.1831 | 2.1 | 2.1 | 1129.84 | InService | 0.95 | 0-Normal | Elhub=2.183 ≈ Plan=2.100 (ratio=104%)
2025-02-27 12:00 | 2.1843 | 2.1 | 1.9 | 796.66 | InService | 0.95 | 0-Normal | Elhub=2.184 ≈ Plan=2.100 (ratio=104%)
2025-02-27 13:00 | 2.1842 | 2.1 | 1.9 | 788.83 | InService | 0.95 | 0-Normal | Elhub=2.184 ≈ Plan=2.100 (ratio=104%)
2025-02-27 14:00 | 2.1828 | 2.1 | 1.8 | 704.1 | InService | 0.95 | 0-Normal | Elhub=2.183 ≈ Plan=2.100 (ratio=104%)
2025-02-27 15:00 | 2.1836 | 2.1 | 2 | 755.52 | InService | 0.95 | 0-Normal | Elhub=2.184 ≈ Plan=2.100 (ratio=104%)
2025-02-27 16:00 | 2.1433 | 2.1 | 2 | 1624.75 | InService | 0.95 | 0-Normal | Elhub=2.143 ≈ Plan=2.100 (ratio=102%)
2025-02-27 17:00 | 2.141 | 2.1 | 2 | 1898.91 | InService | 0.95 | 0-Normal | Elhub=2.141 ≈ Plan=2.100 (ratio=102%)
2025-02-27 18:00 | 2.1674 | 2.1 | 2 | 1156.36 | InService | 0.95 | 0-Normal | Elhub=2.167 ≈ Plan=2.100 (ratio=103%)
2025-02-27 19:00 | 2.1404 | 2.1 | 1.8 | 700.83 | InService | 0.95 | 0-Normal | Elhub=2.140 ≈ Plan=2.100 (ratio=102%)
2025-02-27 20:00 | 2.1639 | 2.1 | 1.8 | 638.07 | InService | 0.95 | 0-Normal | Elhub=2.164 ≈ Plan=2.100 (ratio=103%)
2025-02-27 21:00 | 2.1411 | 2.1 | 0 | 597.06 | InService | 0.95 | 0-Normal | Elhub=2.141 ≈ Plan=2.100 (ratio=102%)
2025-02-27 22:00 | 2.1404 | 2.1 | 0 | 580.81 | InService | 0.95 | 0-Normal | Elhub=2.140 ≈ Plan=2.100 (ratio=102%)
2025-02-27 23:00 | 2.1399 | 2.1 | 2.1 | 545.25 | InService | 0.95 | 0-Normal | Elhub=2.140 ≈ Plan=2.100 (ratio=102%)
2025-02-28 | 2.1577 | 2.1 | 2.1 | 526.3 | InService | 0.95 | 0-Normal | Elhub=2.158 ≈ Plan=2.100 (ratio=103%)
2025-02-28 01:00 | 2.1456 | 2.1 | 2.1 | 525.6 | InService | 0.95 | 0-Normal | Elhub=2.146 ≈ Plan=2.100 (ratio=102%)
2025-02-28 02:00 | 2.1428 | 2.1 | 2.1 | 525.37 | InService | 0.95 | 0-Normal | Elhub=2.143 ≈ Plan=2.100 (ratio=102%)
2025-02-28 03:00 | 2.1433 | 2.1 | 2.1 | 525.83 | InService | 0.95 | 0-Normal | Elhub=2.143 ≈ Plan=2.100 (ratio=102%)
2025-02-28 04:00 | 2.1433 | 2.1 | 2.1 | 545.49 | InService | 0.95 | 0-Normal | Elhub=2.143 ≈ Plan=2.100 (ratio=102%)
2025-02-28 05:00 | 2.1435 | 2.1 | 2.1 | 573.56 | InService | 0.95 | 0-Normal | Elhub=2.144 ≈ Plan=2.100 (ratio=102%)
2025-02-28 06:00 | 2.143 | 2.1 | 2.1 | 1164.91 | InService | 0.95 | 0-Normal | Elhub=2.143 ≈ Plan=2.100 (ratio=102%)
2025-02-28 07:00 | 2.1427 | 2.1 | 2.1 | 1558.55 | InService | 0.95 | 0-Normal | Elhub=2.143 ≈ Plan=2.100 (ratio=102%)
2025-02-28 08:00 | 2.1414 | 2.1 | 2.1 | 1351.73 | InService | 0.95 | 0-Normal | Elhub=2.141 ≈ Plan=2.100 (ratio=102%)
2025-02-28 09:00 | 2.1416 | 2.1 | 2.1 | 1187.37 | InService | 0.95 | 0-Normal | Elhub=2.142 ≈ Plan=2.100 (ratio=102%)
2025-02-28 10:00 | 2.1411 | 2.1 | 2.1 | 716.05 | InService | 0.95 | 0-Normal | Elhub=2.141 ≈ Plan=2.100 (ratio=102%)
2025-02-28 11:00 | 1.6064 | 2.1 | 2.1 | 583.16 | ForcedDerating | 0.65 | D1-ForcedDerating | Elhub=1.606 = 76% av Plan=2.100 – redusert kapasitet
2025-02-28 12:00 | 2.1416 | 2.1 | 2.1 | 573.68 | InService | 0.95 | 0-Normal | Elhub=2.142 ≈ Plan=2.100 (ratio=102%)
2025-02-28 13:00 | 2.1407 | 2.1 | 2.1 | 573.1 | InService | 0.95 | 0-Normal | Elhub=2.141 ≈ Plan=2.100 (ratio=102%)
2025-02-28 14:00 | 2.1414 | 2.1 | 2.1 | 568.18 | InService | 0.95 | 0-Normal | Elhub=2.141 ≈ Plan=2.100 (ratio=102%)
2025-02-28 15:00 | 2.1381 | 2.1 | 2.1 | 574.62 | InService | 0.95 | 0-Normal | Elhub=2.138 ≈ Plan=2.100 (ratio=102%)
2025-02-28 16:00 | 2.138 | 2.1 | 2.1 | 923.46 | InService | 0.95 | 0-Normal | Elhub=2.138 ≈ Plan=2.100 (ratio=102%)
2025-02-28 17:00 | 2.1376 | 2.1 | 2.1 | 1529.43 | InService | 0.95 | 0-Normal | Elhub=2.138 ≈ Plan=2.100 (ratio=102%)
2025-02-28 18:00 | 2.1394 | 2.1 | 2.1 | 663.06 | InService | 0.95 | 0-Normal | Elhub=2.139 ≈ Plan=2.100 (ratio=102%)
2025-02-28 19:00 | 2.1406 | 2.1 | 2.1 | 568.3 | InService | 0.95 | 0-Normal | Elhub=2.141 ≈ Plan=2.100 (ratio=102%)
2025-02-28 20:00 | 2.1398 | 2.1 | 2.1 | 553.21 | InService | 0.95 | 0-Normal | Elhub=2.140 ≈ Plan=2.100 (ratio=102%)
2025-02-28 21:00 | 2.1421 | 2.1 | 2.1 | 547.13 | InService | 0.95 | 0-Normal | Elhub=2.142 ≈ Plan=2.100 (ratio=102%)
2025-02-28 22:00 | 2.1416 | 2.1 | 2.1 | 526.77 | InService | 0.95 | 0-Normal | Elhub=2.142 ≈ Plan=2.100 (ratio=102%)

## Plan vs Bud vs Elhub
3-veis sammenligning: Produksjonplan, Spotbud, Elhub
Time (UTC) | Plan (MWh) | Spotbud (MWh) | Elhub (MWh) | Plan−Elhub | Bud−Elhub
2025-01-31 23:00 | 0 | 0 | 0 | 0 | 0
2025-02-01 | 0 | 0 | 0 | 0 | 0
2025-02-01 01:00 | 0 | 0 | 0 | 0 | 0
2025-02-01 02:00 | 0 | 0 | 0 | 0 | 0
2025-02-01 03:00 | 0 | 0 | 0 | 0 | 0
2025-02-01 04:00 | 0 | 0 | 0 | 0 | 0
2025-02-01 05:00 | 0 | 0 | 0 | 0 | 0
2025-02-01 06:00 | 0 | 0 | 0 | 0 | 0
2025-02-01 07:00 | 2 | 2 | 1.1284 | 0.87162 | 0.87162
2025-02-01 08:00 | 2.1 | 2.2 | 2.1937 | -0.09373 | 0.00627
2025-02-01 09:00 | 2.1 | 2.2 | 2.197 | -0.09702 | 0.00298
2025-02-01 10:00 | 2.1 | 2.2 | 2.1944 | -0.09443 | 0.00557
2025-02-01 11:00 | 2.1 | 2.2 | 2.1935 | -0.09351 | 0.00649
2025-02-01 12:00 | 2.1 | 2.2 | 2.1907 | -0.09075 | 0.00925
2025-02-01 13:00 | 2.1 | 2.2 | 2.1901 | -0.09011 | 0.00989
2025-02-01 14:00 | 2.1 | 2.2 | 2.1886 | -0.08864 | 0.01136
2025-02-01 15:00 | 2.1 | 2.2 | 2.1881 | -0.08807 | 0.01193
2025-02-01 16:00 | 0.5 | 2.2 | 0.65177 | -0.15177 | 1.5482
2025-02-01 17:00 | 2.1 | 2.2 | 2.0392 | 0.06077 | 0.16077
2025-02-01 18:00 | 0.5 | 2.2 | 0.63744 | -0.13744 | 1.5626
2025-02-01 19:00 | 1.4 | 1.4 | 1.4125 | -0.01248 | -0.01248
2025-02-01 20:00 | 1.4 | 1.4 | 1.4272 | -0.0272 | -0.0272
2025-02-01 21:00 | 1.4 | 1.4 | 1.4256 | -0.02564 | -0.02564
2025-02-01 22:00 | 1.4 | 1.4 | 1.4296 | -0.0296 | -0.0296
2025-02-01 23:00 | 0 | 0 | 0.01792 | -0.01792 | -0.01792
2025-02-02 | 0 | 0 | 0 | 0 | 0
2025-02-02 01:00 | 0 | 0 | 0 | 0 | 0
2025-02-02 02:00 | 0 | 0 | 0 | 0 | 0
2025-02-02 03:00 | 0 | 0 | 0 | 0 | 0
2025-02-02 04:00 | 0 | 0 | 0 | 0 | 0
2025-02-02 05:00 | 0 | 0 | 0 | 0 | 0
2025-02-02 06:00 | 0 | 0 | 0 | 0 | 0
2025-02-02 07:00 | 0 | 0 | 0 | 0 | 0
2025-02-02 08:00 | 0 | 0 | 0 | 0 | 0
2025-02-02 09:00 | 0 | 0 | 0 | 0 | 0
2025-02-02 10:00 | 0 | 0 | 0 | 0 | 0
2025-02-02 11:00 | 0 | 0 | 0 | 0 | 0
2025-02-02 12:00 | 0 | 0 | 0 | 0 | 0
2025-02-02 13:00 | 0 | 0 | 0 | 0 | 0
2025-02-02 14:00 | 0 | 0 | 0.019936 | -0.019936 | -0.019936
2025-02-02 15:00 | 2.1 | 2.2 | 0.4575 | 1.6425 | 1.7425
2025-02-02 16:00 | 2.1 | 2.2 | 0.10188 | 1.9981 | 2.0981
2025-02-02 17:00 | 2.1 | 2.2 | 0.05812 | 2.0419 | 2.1419
2025-02-02 18:00 | 2.1 | 2.2 | 0 | 2.1 | 2.2
2025-02-02 19:00 | 2.1 | 2.2 | 0 | 2.1 | 2.2
2025-02-02 20:00 | 0 | 2.2 | 0 | 0 | 2.2
2025-02-02 21:00 | 0 | 1.8 | 0 | 0 | 1.8
2025-02-02 22:00 | 0 | 0 | 0 | 0 | 0
2025-02-02 23:00 | 0 | 0 | 0 | 0 | 0
2025-02-03 | 0 | 0 | 0 | 0 | 0
2025-02-03 01:00 | 0 | 0 | 0 | 0 | 0
2025-02-03 02:00 | 0 | 0 | 0 | 0 | 0
2025-02-03 03:00 | 0 | 0 | 0 | 0 | 0
2025-02-03 04:00 | 0 | 0 | 0 | 0 | 0
2025-02-03 05:00 | 0 | 0 | 0 | 0 | 0
2025-02-03 06:00 | 0 | 0 | 0 | 0 | 0
2025-02-03 07:00 | 0 | 2.2 | 0 | 0 | 2.2
2025-02-03 08:00 | 0 | 2.2 | 0 | 0 | 2.2
2025-02-03 09:00 | 0 | 2.2 | 0 | 0 | 2.2
2025-02-03 10:00 | 2.1 | 2.2 | 0 | 2.1 | 2.2
2025-02-03 11:00 | 2.1 | 2.2 | 0 | 2.1 | 2.2
2025-02-03 12:00 | 2.1 | 2.2 | 0 | 2.1 | 2.2
2025-02-03 13:00 | 0 | 2.2 | 0.008 | -0.008 | 2.192
2025-02-03 14:00 | 0 | 2.2 | 0 | 0 | 2.2
2025-02-03 15:00 | 2.1 | 2.2 | 0 | 2.1 | 2.2
2025-02-03 16:00 | 0 | 2.2 | 0 | 0 | 2.2
2025-02-03 17:00 | 0 | 2.2 | 0 | 0 | 2.2
2025-02-03 18:00 | 0 | 2.2 | 0 | 0 | 2.2
2025-02-03 19:00 | 0 | 2.2 | 0 | 0 | 2.2
2025-02-03 20:00 | 0 | 2.2 | 0 | 0 | 2.2
2025-02-03 21:00 | 0 | 2 | 0 | 0 | 2
2025-02-03 22:00 | 0 | 0 | 0 | 0 | 0
2025-02-03 23:00 | 0 | 0 | 0 | 0 | 0
2025-02-04 | 0 | 0 | 0 | 0 | 0
2025-02-04 01:00 | 0 | 0 | 0 | 0 | 0
2025-02-04 02:00 | 0 | 0 | 0 | 0 | 0
2025-02-04 03:00 | 0 | 1.5 | 0 | 0 | 1.5
2025-02-04 04:00 | 0 | 1.5 | 0 | 0 | 1.5
2025-02-04 05:00 | 0 | 1.9 | 0 | 0 | 1.9
2025-02-04 06:00 | 0 | 2.2 | 0 | 0 | 2.2
2025-02-04 07:00 | 0 | 2.2 | 0 | 0 | 2.2
2025-02-04 08:00 | 0 | 2.2 | 0 | 0 | 2.2
2025-02-04 09:00 | 0 | 2.2 | 0 | 0 | 2.2
2025-02-04 10:00 | 0 | 2.2 | 0.43786 | -0.43786 | 1.7621
2025-02-04 11:00 | 0 | 2.2 | 1.997 | -1.997 | 0.20304
2025-02-04 12:00 | 0 | 2.2 | 1.9992 | -1.9992 | 0.20084
2025-02-04 13:00 | 0 | 2.2 | 1.9991 | -1.9991 | 0.20089
2025-02-04 14:00 | 0 | 2.2 | 1.9974 | -1.9974 | 0.20256
2025-02-04 15:00 | 2.1 | 2.2 | 2.0004 | 0.09962 | 0.19962
2025-02-04 16:00 | 2.1 | 2.2 | 1.9995 | 0.10051 | 0.20051
2025-02-04 17:00 | 2.1 | 2.2 | 2.1333 | -0.03331 | 0.06669
2025-02-04 18:00 | 2.1 | 2.2 | 2.1918 | -0.09184 | 0.00816
2025-02-04 19:00 | 2.1 | 0 | 2.1913 | -0.0913 | -2.1913
2025-02-04 20:00 | 2.1 | 0 | 2.193 | -0.09296 | -2.193
2025-02-04 21:00 | 2.1 | 0 | 2.1414 | -0.04137 | -2.1414
2025-02-04 22:00 | 1.7 | 0 | 1.7531 | -0.05312 | -1.7531
2025-02-04 23:00 | 1.7 | 1.7 | 1.7355 | -0.03552 | -0.03552
2025-02-05 | 1.7 | 1.7 | 1.7369 | -0.0369 | -0.0369
2025-02-05 01:00 | 1.7 | 1.7 | 2.1562 | -0.45619 | -0.45619
2025-02-05 02:00 | 2.1 | 1.7 | 2.1811 | -0.08106 | -0.48106
2025-02-05 03:00 | 2.1 | 2.1 | 2.1801 | -0.08013 | -0.08013
2025-02-05 04:00 | 2.1 | 2.1 | 2.1814 | -0.08144 | -0.08144
2025-02-05 05:00 | 2.1 | 2.1 | 2.1814 | -0.08137 | -0.08137
2025-02-05 06:00 | 2.1 | 2.1 | 2.1815 | -0.08147 | -0.08147
2025-02-05 07:00 | 2.1 | 2.2 | 2.1804 | -0.08039 | 0.01961
2025-02-05 08:00 | 2.1 | 2.2 | 2.1826 | -0.08256 | 0.01744
2025-02-05 09:00 | 2.1 | 2.2 | 2.1815 | -0.0815 | 0.0185
2025-02-05 10:00 | 2.1 | 2.2 | 2.1816 | -0.08157 | 0.01843
2025-02-05 11:00 | 2.1 | 2.1 | 2.1815 | -0.08147 | -0.08147
2025-02-05 12:00 | 2.1 | 2.1 | 2.1818 | -0.08176 | -0.08176
2025-02-05 13:00 | 2.1 | 2.1 | 2.1824 | -0.08237 | -0.08237
2025-02-05 14:00 | 2.1 | 2.1 | 2.1821 | -0.08211 | -0.08211
2025-02-05 15:00 | 2.1 | 2.2 | 2.1821 | -0.08211 | 0.01789
2025-02-05 16:00 | 2.1 | 2.2 | 2.1818 | -0.0818 | 0.0182
2025-02-05 17:00 | 2.1 | 2.2 | 2.1824 | -0.08236 | 0.01764
2025-02-05 18:00 | 2.1 | 2.2 | 2.1802 | -0.08023 | 0.01977
2025-02-05 19:00 | 2.1 | 0 | 2.1827 | -0.08272 | -2.1827
2025-02-05 20:00 | 2.1 | 1.8 | 2.1827 | -0.08265 | -0.38265
2025-02-05 21:00 | 2.1 | 0 | 2.1826 | -0.08256 | -2.1826
2025-02-05 22:00 | 2.1 | 0 | 2.1818 | -0.0818 | -2.1818
2025-02-05 23:00 | 2.2 | 2.2 | 2.1854 | 0.01463 | 0.01463
2025-02-06 | 2.12 | 2.2 | 2.1825 | -0.06252 | 0.01748
2025-02-06 01:00 | 2.099 | 2.2 | 2.1832 | -0.0842 | 0.0168
2025-02-06 02:00 | 2.078 | 2.2 | 2.182 | -0.10405 | 0.01795
2025-02-06 03:00 | 2.057 | 2.2 | 2.1834 | -0.12643 | 0.01657
2025-02-06 04:00 | 2.036 | 2.2 | 2.1815 | -0.1455 | 0.0185
2025-02-06 05:00 | 2.016 | 2.2 | 2.1818 | -0.16576 | 0.01824
2025-02-06 06:00 | 1.996 | 2.2 | 2.1808 | -0.18477 | 0.01923
2025-02-06 07:00 | 2.103 | 2.2 | 2.1818 | -0.07885 | 0.01815
2025-02-06 08:00 | 2.123 | 2.2 | 2.1804 | -0.05742 | 0.01958
2025-02-06 09:00 | 2.113 | 2.2 | 2.1806 | -0.06758 | 0.01942
2025-02-06 10:00 | 2.121 | 2.2 | 2.1803 | -0.05932 | 0.01968
2025-02-06 11:00 | 2.2 | 2.2 | 2.1785 | 0.02154 | 0.02154
2025-02-06 12:00 | 2.2 | 2.2 | 2.1797 | 0.02026 | 0.02026
2025-02-06 13:00 | 2.2 | 2.2 | 2.181 | 0.019 | 0.019
2025-02-06 14:00 | 2.2 | 2.2 | 2.1807 | 0.0193 | 0.0193
2025-02-06 15:00 | 2.2 | 2.2 | 2.181 | 0.01901 | 0.01901
2025-02-06 16:00 | 2.2 | 2.2 | 2.1796 | 0.02041 | 0.02041
2025-02-06 17:00 | 2.2 | 2.2 | 2.1795 | 0.02055 | 0.02055
2025-02-06 18:00 | 2.2 | 2.2 | 2.1783 | 0.02166 | 0.02166
2025-02-06 19:00 | 2.2 | 2.2 | 2.1778 | 0.02215 | 0.02215
2025-02-06 20:00 | 2.2 | 2.2 | 2.1774 | 0.02262 | 0.02262
2025-02-06 21:00 | 2.2 | 2.2 | 2.1761 | 0.0239 | 0.0239
2025-02-06 22:00 | 2.2 | 2.2 | 2.1747 | 0.02535 | 0.02535
2025-02-06 23:00 | 2.2 | 2.2 | 2.1759 | 0.02406 | 0.02406
2025-02-07 | 2.105 | 2.2 | 2.1768 | -0.0718 | 0.0232
2025-02-07 01:00 | 2.084 | 2.2 | 2.174 | -0.09005 | 0.02595
2025-02-07 02:00 | 2.063 | 2.2 | 2.1749 | -0.11188 | 0.02512
2025-02-07 03:00 | 2.042 | 2.2 | 2.1747 | -0.13265 | 0.02535
2025-02-07 04:00 | 2.022 | 2.2 | 2.1747 | -0.15275 | 0.02525
2025-02-07 05:00 | 2.002 | 2.2 | 2.1733 | -0.17132 | 0.02668
2025-02-07 06:00 | 1.982 | 2.2 | 2.1737 | -0.19169 | 0.02631
2025-02-07 07:00 | 2.093 | 2.2 | 2.1731 | -0.08012 | 0.02688
2025-02-07 08:00 | 2.105 | 2.2 | 2.1723 | -0.06726 | 0.02774
2025-02-07 09:00 | 2.099 | 2.2 | 2.1712 | -0.07217 | 0.02883
2025-02-07 10:00 | 2.098 | 2.2 | 2.1701 | -0.07214 | 0.02986
2025-02-07 11:00 | 2.2 | 2.2 | 2.1691 | 0.03088 | 0.03088
2025-02-07 12:00 | 2.2 | 2.2 | 2.169 | 0.03104 | 0.03104
2025-02-07 13:00 | 2.2 | 2.2 | 2.1692 | 0.03085 | 0.03085
2025-02-07 14:00 | 2.2 | 2.2 | 2.1681 | 0.03193 | 0.03193
2025-02-07 15:00 | 2.2 | 2.2 | 2.1672 | 0.03277 | 0.03277
2025-02-07 16:00 | 2.2 | 2.2 | 2.1677 | 0.03232 | 0.03232
2025-02-07 17:00 | 2.2 | 2.2 | 2.1638 | 0.03623 | 0.03623
2025-02-07 18:00 | 2.2 | 2.2 | 2.166 | 0.03398 | 0.03398
2025-02-07 19:00 | 1.8 | 1.8 | 1.8459 | -0.04589 | -0.04589
2025-02-07 20:00 | 1.8 | 1.8 | 1.838 | -0.03798 | -0.03798
2025-02-07 21:00 | 1.8 | 1.8 | 1.8363 | -0.03635 | -0.03635
2025-02-07 22:00 | 1.8 | 1.8 | 1.8364 | -0.03639 | -0.03639
2025-02-07 23:00 | 0 | 0 | 0.020834 | -0.020834 | -0.020834
2025-02-08 | 1.787 | 0 | 0 | 1.787 | 0
2025-02-08 01:00 | 1.769 | 0 | 0 | 1.769 | 0
2025-02-08 02:00 | 1.751 | 0 | 0 | 1.751 | 0
2025-02-08 03:00 | 1.733 | 0 | 0 | 1.733 | 0
2025-02-08 04:00 | 1.716 | 0 | 0 | 1.716 | 0
2025-02-08 05:00 | 1.699 | 0 | 0 | 1.699 | 0
2025-02-08 06:00 | 1.682 | 0 | 0 | 1.682 | 0
2025-02-08 07:00 | 0 | 0 | 0 | 0 | 0
2025-02-08 08:00 | 0 | 0 | 0 | 0 | 0
2025-02-08 09:00 | 0 | 0 | 0 | 0 | 0
2025-02-08 10:00 | 0 | 0 | 0.013792 | -0.013792 | -0.013792
2025-02-08 11:00 | 0.6 | 0.6 | 0.60784 | -0.00784 | -0.00784
2025-02-08 12:00 | 0.6 | 0.6 | 0.60912 | -0.00912 | -0.00912
2025-02-08 13:00 | 0.6 | 0.6 | 0.61347 | -0.01347 | -0.01347
2025-02-08 14:00 | 0.6 | 0.6 | 0.61709 | -0.01709 | -0.01709
2025-02-08 15:00 | 2.2 | 2.2 | 2.1384 | 0.06157 | 0.06157
2025-02-08 16:00 | 2.2 | 2.2 | 2.1947 | 0.00525 | 0.00525
2025-02-08 17:00 | 2.2 | 2.2 | 2.1836 | 0.01642 | 0.01642
2025-02-08 18:00 | 2.2 | 2.2 | 2.1816 | 0.0184 | 0.0184
2025-02-08 19:00 | 1.7 | 1.7 | 1.8528 | -0.1528 | -0.1528
2025-02-08 20:00 | 0.7 | 0.7 | 0.74132 | -0.04132 | -0.04132
2025-02-08 21:00 | 0.7 | 0.7 | 0.71126 | -0.01126 | -0.01126
2025-02-08 22:00 | 0.7 | 0.7 | 0.71149 | -0.01149 | -0.01149
2025-02-08 23:00 | 1.3 | 1.3 | 1.3094 | -0.00941 | -0.00941
2025-02-09 | 0.689 | 1.3 | 1.3258 | -0.63684 | -0.025842
2025-02-09 01:00 | 0.682 | 1.3 | 1.3244 | -0.64239 | -0.02439
2025-02-09 02:00 | 0.675 | 1.3 | 1.3244 | -0.64941 | -0.02441
2025-02-09 03:00 | 0.668 | 0 | 0.015366 | 0.65263 | -0.015366
2025-02-09 04:00 | 0.662 | 0 | 0 | 0.662 | 0
2025-02-09 05:00 | 0.655 | 0 | 0 | 0.655 | 0
2025-02-09 06:00 | 0.649 | 0 | 0.024256 | 0.62474 | -0.024256
2025-02-09 07:00 | 1.28 | 1.9 | 1.9265 | -0.64652 | -0.02652
2025-02-09 08:00 | 1.28 | 2 | 2.0338 | -0.75383 | -0.03383
2025-02-09 09:00 | 1.901 | 2 | 2.0383 | -0.13733 | -0.03833
2025-02-09 10:00 | 1.971 | 1.9 | 1.9417 | 0.02933 | -0.04167
2025-02-09 11:00 | 2.2 | 2.2 | 2.1807 | 0.01927 | 0.01927
2025-02-09 12:00 | 2.2 | 2.2 | 2.1877 | 0.01228 | 0.01228
2025-02-09 13:00 | 2.2 | 2.2 | 2.1871 | 0.01287 | 0.01287
2025-02-09 14:00 | 2.2 | 2.2 | 2.1848 | 0.01523 | 0.01523
2025-02-09 15:00 | 2.2 | 2.2 | 2.1859 | 0.01414 | 0.01414
2025-02-09 16:00 | 2.2 | 2.2 | 2.1838 | 0.0162 | 0.0162
2025-02-09 17:00 | 2.2 | 2.2 | 2.183 | 0.01699 | 0.01699
2025-02-09 18:00 | 2.2 | 2.2 | 2.1817 | 0.01827 | 0.01827
2025-02-09 19:00 | 0 | 0 | 0.034052 | -0.034052 | -0.034052
2025-02-09 20:00 | 0 | 0 | 0 | 0 | 0
2025-02-09 21:00 | 0 | 0 | 0 | 0 | 0
2025-02-09 22:00 | 0 | 0 | 0 | 0 | 0
2025-02-09 23:00 | 0 | 0 | 0 | 0 | 0
2025-02-10 | 2.121 | 0 | 0 | 2.121 | 0
2025-02-10 01:00 | 2.1 | 0 | 0 | 2.1 | 0
2025-02-10 02:00 | 2.079 | 0 | 0 | 2.079 | 0
2025-02-10 03:00 | 2.058 | 0 | 0 | 2.058 | 0
2025-02-10 04:00 | 2.037 | 0 | 0 | 2.037 | 0
2025-02-10 05:00 | 2.017 | 0 | 0 | 2.017 | 0
2025-02-10 06:00 | 1.997 | 0 | 0.013728 | 1.9833 | -0.013728
2025-02-10 07:00 | 0 | 1.8 | 1.8224 | -1.8224 | -0.0224
2025-02-10 08:00 | 0 | 1.8 | 1.8362 | -1.8362 | -0.03619
2025-02-10 09:00 | 1.794 | 0 | 0.62969 | 1.1643 | -0.62969
2025-02-10 10:00 | 1.784 | 0 | 0.6041 | 1.1799 | -0.6041
2025-02-10 11:00 | 1.3 | 1.3 | 1.3093 | -0.00931 | -0.00931
2025-02-10 12:00 | 1.3 | 1.3 | 1.0187 | 0.28134 | 0.28134
2025-02-10 13:00 | 1.3 | 1.3 | 1.3269 | -0.02691 | -0.02691
2025-02-10 14:00 | 1.3 | 1.3 | 1.3289 | -0.02889 | -0.02889
2025-02-10 15:00 | 0 | 0 | 0.011176 | -0.011176 | -0.011176
2025-02-10 16:00 | 0 | 0 | 0 | 0 | 0
2025-02-10 17:00 | 0 | 0 | 0 | 0 | 0
2025-02-10 18:00 | 0 | 0 | 0 | 0 | 0
2025-02-10 19:00 | 0 | 0 | 0 | 0 | 0
2025-02-10 20:00 | 0 | 0 | 0 | 0 | 0
2025-02-10 21:00 | 0 | 0 | 0 | 0 | 0
2025-02-10 22:00 | 0 | 0 | 0 | 0 | 0
2025-02-10 23:00 | 0 | 0 | 0 | 0 | 0
2025-02-11 | 1.284 | 0 | 0 | 1.284 | 0
2025-02-11 01:00 | 1.271 | 0 | 0 | 1.271 | 0
2025-02-11 02:00 | 1.258 | 0 | 0 | 1.258 | 0
2025-02-11 03:00 | 1.246 | 0 | 0 | 1.246 | 0
2025-02-11 04:00 | 1.234 | 0 | 0 | 1.234 | 0
2025-02-11 05:00 | 1.222 | 0 | 0 | 1.222 | 0
2025-02-11 06:00 | 1.21 | 0 | 0 | 1.21 | 0
2025-02-11 07:00 | 0 | 0 | 0 | 0 | 0
2025-02-11 08:00 | 0 | 0 | 0 | 0 | 0
2025-02-11 09:00 | 0 | 0 | 0 | 0 | 0
2025-02-11 10:00 | 0 | 0 | 0 | 0 | 0
2025-02-11 11:00 | 0 | 0 | 0 | 0 | 0
2025-02-11 12:00 | 0 | 0 | 0 | 0 | 0
2025-02-11 13:00 | 0 | 0 | 0 | 0 | 0
2025-02-11 14:00 | 0 | 0 | 0 | 0 | 0
2025-02-11 15:00 | 0 | 0 | 0 | 0 | 0
2025-02-11 16:00 | 0 | 0 | 0 | 0 | 0
2025-02-11 17:00 | 0 | 0 | 0 | 0 | 0
2025-02-11 18:00 | 0 | 0 | 0 | 0 | 0
2025-02-11 19:00 | 0 | 0 | 0 | 0 | 0
2025-02-11 20:00 | 0 | 0 | 0 | 0 | 0
2025-02-11 21:00 | 0 | 0 | 0 | 0 | 0
2025-02-11 22:00 | 0 | 0 | 0 | 0 | 0
2025-02-11 23:00 | 0 | 0 | 0 | 0 | 0
2025-02-12 | 0 | 0 | 0 | 0 | 0
2025-02-12 01:00 | 0 | 0 | 0 | 0 | 0
2025-02-12 02:00 | 0 | 0 | 0.001504 | -0.001504 | -0.001504
2025-02-12 03:00 | 0 | 1.4 | 1.3995 | -1.3995 | 0.00055
2025-02-12 04:00 | 0 | 1.4 | 1.4301 | -1.4301 | -0.03005
2025-02-12 05:00 | 0 | 1.4 | 1.4271 | -1.4271 | -0.02714
2025-02-12 06:00 | 0 | 1.4 | 1.4263 | -1.4263 | -0.02633
2025-02-12 07:00 | 1.395 | 2 | 2.0192 | -0.6242 | -0.0192
2025-02-12 08:00 | 1.381 | 2 | 2.0419 | -0.66089 | -0.04189
2025-02-12 09:00 | 1.965 | 1.8 | 1.8447 | 0.12033 | -0.04467
2025-02-12 10:00 | 1.982 | 1.6 | 1.6396 | 0.34241 | -0.03959
2025-02-12 11:00 | 0 | 0 | 0.63148 | -0.63148 | -0.63148
2025-02-12 12:00 | 1.8 | 1.8 | 1.8045 | -0.00445 | -0.00445
2025-02-12 13:00 | 1.8 | 1.8 | 1.8357 | -0.03565 | -0.03565
2025-02-12 14:00 | 1.9 | 1.9 | 1.9341 | -0.03408 | -0.03408
2025-02-12 15:00 | 2.2 | 2.2 | 2.1891 | 0.01094 | 0.01094
2025-02-12 16:00 | 2.2 | 2.2 | 2.1975 | 0.0025 | 0.0025
2025-02-12 17:00 | 2.2 | 2.2 | 2.1967 | 0.00333 | 0.00333
2025-02-12 18:00 | 2.2 | 2.2 | 2.1956 | 0.00441 | 0.00441
2025-02-12 19:00 | 0.6 | 0.6 | 0.65888 | -0.05888 | -0.05888
2025-02-12 20:00 | 0.6 | 0.6 | 0.61772 | -0.01772 | -0.01772
2025-02-12 21:00 | 0.6 | 0.6 | 0.61776 | -0.01776 | -0.01776
2025-02-12 22:00 | 0.6 | 0.6 | 0.61709 | -0.01709 | -0.01709
2025-02-12 23:00 | 0 | 0 | 0.004774 | -0.004774 | -0.004774
2025-02-13 | 0 | 0 | 0 | 0 | 0
2025-02-13 01:00 | 0 | 0 | 0 | 0 | 0
2025-02-13 02:00 | 0 | 0 | 0 | 0 | 0
2025-02-13 03:00 | 0 | 0 | 0 | 0 | 0
2025-02-13 04:00 | 0 | 0 | 0 | 0 | 0
2025-02-13 05:00 | 0 | 0 | 0 | 0 | 0
2025-02-13 06:00 | 0 | 0 | 0.065952 | -0.065952 | -0.065952
2025-02-13 07:00 | 2.1 | 2.1 | 2.1334 | -0.0334 | -0.0334
2025-02-13 08:00 | 2.1 | 2.1 | 2.143 | -0.04304 | -0.04304
2025-02-13 09:00 | 2.1 | 2.1 | 2.1413 | -0.04128 | -0.04128
2025-02-13 10:00 | 2.1 | 2.1 | 0.031848 | 2.0682 | 2.0682
2025-02-13 11:00 | 0 | 0 | 0 | 0 | 0
2025-02-13 12:00 | 0 | 0 | 0 | 0 | 0
2025-02-13 13:00 | 0 | 0 | 0 | 0 | 0
2025-02-13 14:00 | 0 | 0 | 0.050144 | -0.050144 | -0.050144
2025-02-13 15:00 | 1.8 | 1.8 | 1.834 | -0.03398 | -0.03398
2025-02-13 16:00 | 1.8 | 1.8 | 1.834 | -0.03398 | -0.03398
2025-02-13 17:00 | 0.5 | 1.8 | 0.63744 | -0.13744 | 1.1626
2025-02-13 18:00 | 1.8 | 1.8 | 1.7973 | 0.00272 | 0.00272
2025-02-13 19:00 | 0 | 0 | 0.02148 | -0.02148 | -0.02148
2025-02-13 20:00 | 0 | 0 | 0 | 0 | 0
2025-02-13 21:00 | 0 | 0 | 0 | 0 | 0
2025-02-13 22:00 | 0 | 0 | 0 | 0 | 0
2025-02-13 23:00 | 0 | 0 | 0 | 0 | 0
2025-02-14 | 0 | 0 | 0 | 0 | 0
2025-02-14 01:00 | 0 | 0 | 0 | 0 | 0
2025-02-14 02:00 | 0 | 0 | 0 | 0 | 0
2025-02-14 03:00 | 0 | 0 | 0 | 0 | 0
2025-02-14 04:00 | 0 | 0 | 0 | 0 | 0
2025-02-14 05:00 | 0 | 0 | 0 | 0 | 0
2025-02-14 06:00 | 0 | 0 | 0.010976 | -0.010976 | -0.010976
2025-02-14 07:00 | 2.1 | 2.1 | 2.1178 | -0.01779 | -0.01779
2025-02-14 08:00 | 2.1 | 2.1 | 2.1445 | -0.04448 | -0.04448
2025-02-14 09:00 | 2.1 | 2.1 | 2.1425 | -0.04246 | -0.04246
2025-02-14 10:00 | 2 | 2 | 2.0409 | -0.04093 | -0.04093
2025-02-14 11:00 | 0 | 0 | 0.030468 | -0.030468 | -0.030468
2025-02-14 12:00 | 0 | 0 | 0 | 0 | 0
2025-02-14 13:00 | 0 | 0 | 0 | 0 | 0
2025-02-14 14:00 | 0 | 0 | 0.098848 | -0.098848 | -0.098848
2025-02-14 15:00 | 2.1 | 2.1 | 2.1366 | -0.0366 | -0.0366
2025-02-14 16:00 | 0.5 | 2.1 | 0.65072 | -0.15072 | 1.4493
2025-02-14 17:00 | 0.5 | 2.1 | 0.60231 | -0.10231 | 1.4977
2025-02-14 18:00 | 2.1 | 2.1 | 2.0895 | 0.0105 | 0.0105
2025-02-14 19:00 | 0 | 0 | 0.034918 | -0.034918 | -0.034918
2025-02-14 20:00 | 0 | 0 | 0 | 0 | 0
2025-02-14 21:00 | 0 | 0 | 0 | 0 | 0
2025-02-14 22:00 | 0 | 0 | 0 | 0 | 0
2025-02-14 23:00 | 0 | 0 | 0 | 0 | 0
2025-02-15 | 0 | 0 | 0 | 0 | 0
2025-02-15 01:00 | 0 | 0 | 0 | 0 | 0
2025-02-15 02:00 | 0 | 0 | 0 | 0 | 0
2025-02-15 03:00 | 0 | 0 | 0 | 0 | 0
2025-02-15 04:00 | 0 | 0 | 0 | 0 | 0
2025-02-15 05:00 | 0 | 0 | 0 | 0 | 0
2025-02-15 06:00 | 0 | 0 | 0 | 0 | 0
2025-02-15 07:00 | 0 | 0 | 0 | 0 | 0
2025-02-15 08:00 | 0 | 0 | 0 | 0 | 0
2025-02-15 09:00 | 0 | 0 | 0 | 0 | 0
2025-02-15 10:00 | 0 | 0 | 0 | 0 | 0
2025-02-15 11:00 | 0 | 0 | 0 | 0 | 0
2025-02-15 12:00 | 0 | 0 | 0 | 0 | 0
2025-02-15 13:00 | 0 | 0 | 0 | 0 | 0
2025-02-15 14:00 | 0 | 0 | 0 | 0 | 0
2025-02-15 15:00 | 0 | 0 | 0 | 0 | 0
2025-02-15 16:00 | 1.1 | 1.1 | 0.76995 | 0.33005 | 0.33005
2025-02-15 17:00 | 1.1 | 1.1 | 1.1232 | -0.0232 | -0.0232
2025-02-15 18:00 | 1.1 | 1.1 | 1.122 | -0.02201 | -0.02201
2025-02-15 19:00 | 0 | 0 | 0.012392 | -0.012392 | -0.012392
2025-02-15 20:00 | 0 | 0 | 0 | 0 | 0
2025-02-15 21:00 | 0 | 0 | 0 | 0 | 0
2025-02-15 22:00 | 0 | 0 | 0 | 0 | 0
2025-02-15 23:00 | 0 | 0 | 0 | 0 | 0
2025-02-16 | 0 | 0 | 0 | 0 | 0
2025-02-16 01:00 | 0 | 0 | 0 | 0 | 0
2025-02-16 02:00 | 0 | 0 | 0 | 0 | 0
2025-02-16 03:00 | 0 | 0 | 0 | 0 | 0
2025-02-16 04:00 | 0 | 0 | 0 | 0 | 0
2025-02-16 05:00 | 0 | 0 | 0 | 0 | 0
2025-02-16 06:00 | 0 | 0 | 0 | 0 | 0
2025-02-16 07:00 | 0 | 0 | 0 | 0 | 0
2025-02-16 08:00 | 0 | 0 | 0 | 0 | 0
2025-02-16 09:00 | 0 | 0 | 0 | 0 | 0
2025-02-16 10:00 | 0 | 0 | 0 | 0 | 0
2025-02-16 11:00 | 0 | 0 | 0 | 0 | 0
2025-02-16 12:00 | 0 | 0 | 0 | 0 | 0
2025-02-16 13:00 | 0 | 0 | 0 | 0 | 0
2025-02-16 14:00 | 0 | 0 | 0.016352 | -0.016352 | -0.016352
2025-02-16 15:00 | 1.3 | 1.3 | 1.3172 | -0.01718 | -0.01718
2025-02-16 16:00 | 1.3 | 1.3 | 1.3267 | -0.02666 | -0.02666
2025-02-16 17:00 | 0 | 1.3 | 0.015168 | -0.015168 | 1.2848
2025-02-16 18:00 | 1.3 | 1.3 | 0 | 1.3 | 1.3
2025-02-16 19:00 | 0 | 0 | 0 | 0 | 0
2025-02-16 20:00 | 0 | 0 | 0 | 0 | 0
2025-02-16 21:00 | 0 | 0 | 0 | 0 | 0
2025-02-16 22:00 | 0 | 0 | 0 | 0 | 0
2025-02-16 23:00 | 1.287 | 0 | 0 | 1.287 | 0
2025-02-17 | 1.287 | 0 | 0 | 1.287 | 0
2025-02-17 01:00 | 1.274 | 0 | 0 | 1.274 | 0
2025-02-17 02:00 | 1.261 | 0 | 0 | 1.261 | 0
2025-02-17 03:00 | 1.248 | 0 | 0 | 1.248 | 0
2025-02-17 04:00 | 1.236 | 0 | 0 | 1.236 | 0
2025-02-17 05:00 | 1.224 | 0 | 0 | 1.224 | 0
2025-02-17 06:00 | 1.212 | 0 | 0.041728 | 1.1703 | -0.041728
2025-02-17 07:00 | 0 | 2.1 | 2.1322 | -2.1322 | -0.03225
2025-02-17 08:00 | 0 | 2.1 | 2.1414 | -2.1414 | -0.04141
2025-02-17 09:00 | 2.087 | 2 | 2.045 | 0.04201 | -0.04499
2025-02-17 10:00 | 2.083 | 1.9 | 0.028934 | 2.0541 | 1.8711
2025-02-17 11:00 | 1.973 | 0 | 0 | 1.973 | 0
2025-02-17 12:00 | 1.986 | 0 | 0 | 1.986 | 0
2025-02-17 13:00 | 1.986 | 0 | 0 | 1.986 | 0
2025-02-17 14:00 | 0 | 0 | 0.004576 | -0.004576 | -0.004576
2025-02-17 15:00 | 1.8 | 1.8 | 1.8105 | -0.01052 | -0.01052
2025-02-17 16:00 | 2 | 2 | 2.0325 | -0.03248 | -0.03248
2025-02-17 17:00 | 2.1 | 2.1 | 2.1377 | -0.0377 | -0.0377
2025-02-17 18:00 | 2 | 2 | 2.047 | -0.04698 | -0.04698
2025-02-17 19:00 | 0 | 0 | 0.027328 | -0.027328 | -0.027328
2025-02-17 20:00 | 0 | 0 | 0 | 0 | 0
2025-02-17 21:00 | 0 | 0 | 0 | 0 | 0
2025-02-17 22:00 | 0 | 0 | 0 | 0 | 0
2025-02-17 23:00 | 0 | 0 | 0 | 0 | 0
2025-02-18 | 1.99 | 0 | 0 | 1.99 | 0
2025-02-18 01:00 | 1.97 | 0 | 0 | 1.97 | 0
2025-02-18 02:00 | 1.95 | 0 | 0 | 1.95 | 0
2025-02-18 03:00 | 1.931 | 0 | 0 | 1.931 | 0
2025-02-18 04:00 | 1.912 | 0 | 0 | 1.912 | 0
2025-02-18 05:00 | 1.893 | 0 | 0 | 1.893 | 0
2025-02-18 06:00 | 1.874 | 0 | 0.015296 | 1.8587 | -0.015296
2025-02-18 07:00 | 0 | 1.9 | 1.9236 | -1.9236 | -0.02361
2025-02-18 08:00 | 0 | 1.9 | 1.9388 | -1.9388 | -0.03885
2025-02-18 09:00 | 1.881 | 1.9 | 1.9388 | -0.05778 | -0.03878
2025-02-18 10:00 | 1.866 | 1.8 | 1.8464 | 0.01956 | -0.04644
2025-02-18 11:00 | 0 | 0 | 0.025568 | -0.025568 | -0.025568
2025-02-18 12:00 | 0 | 0 | 0 | 0 | 0
2025-02-18 13:00 | 0 | 0 | 0 | 0 | 0
2025-02-18 14:00 | 0 | 0 | 0 | 0 | 0
2025-02-18 15:00 | 0 | 0 | 0 | 0 | 0
2025-02-18 16:00 | 0 | 0 | 0 | 0 | 0
2025-02-18 17:00 | 0 | 0 | 0 | 0 | 0
2025-02-18 18:00 | 0 | 0 | 0 | 0 | 0
2025-02-18 19:00 | 0 | 0 | 0 | 0 | 0
2025-02-18 20:00 | 0 | 0 | 0 | 0 | 0
2025-02-18 21:00 | 0 | 0 | 0 | 0 | 0
2025-02-18 22:00 | 0 | 0 | 0 | 0 | 0
2025-02-18 23:00 | 0 | 0 | 0 | 0 | 0
2025-02-19 | 0 | 0 | 0 | 0 | 0
2025-02-19 01:00 | 0 | 0 | 0 | 0 | 0
2025-02-19 02:00 | 0 | 0 | 0 | 0 | 0
2025-02-19 03:00 | 0 | 0 | 0 | 0 | 0
2025-02-19 04:00 | 0 | 0 | 0 | 0 | 0
2025-02-19 05:00 | 0 | 0 | 0.000384 | -0.000384 | -0.000384
2025-02-19 06:00 | 1.2 | 0 | 1.1901 | 0.00992 | -1.1901
2025-02-19 07:00 | 1.2 | 1.2 | 1.227 | -0.02704 | -0.02704
2025-02-19 08:00 | 1.2 | 1.2 | 1.2214 | -0.02144 | -0.02144
2025-02-19 09:00 | 0 | 1.2 | 0.01504 | -0.01504 | 1.185
2025-02-19 10:00 | 0 | 1.2 | 0 | 0 | 1.2
2025-02-19 11:00 | 0 | 0 | 0 | 0 | 0
2025-02-19 12:00 | 0 | 0 | 0 | 0 | 0
2025-02-19 13:00 | 0 | 0 | 0 | 0 | 0
2025-02-19 14:00 | 0 | 0 | 0 | 0 | 0
2025-02-19 15:00 | 0 | 0 | 0 | 0 | 0
2025-02-19 16:00 | 0 | 0 | 0 | 0 | 0
2025-02-19 17:00 | 0 | 0 | 0 | 0 | 0
2025-02-19 18:00 | 0 | 0 | 0 | 0 | 0
2025-02-19 19:00 | 0 | 0 | 0 | 0 | 0
2025-02-19 20:00 | 0 | 0 | 0 | 0 | 0
2025-02-19 21:00 | 0 | 0 | 0 | 0 | 0
2025-02-19 22:00 | 0 | 0 | 0 | 0 | 0
2025-02-19 23:00 | 0 | 0 | 0 | 0 | 0
2025-02-20 | 0 | 0 | 0 | 0 | 0
2025-02-20 01:00 | 0 | 0 | 0 | 0 | 0
2025-02-20 02:00 | 0 | 0 | 0 | 0 | 0
2025-02-20 03:00 | 0 | 0 | 0 | 0 | 0
2025-02-20 04:00 | 0 | 0 | 0 | 0 | 0
2025-02-20 05:00 | 0 | 0 | 0 | 0 | 0
2025-02-20 06:00 | 0 | 0 | 0 | 0 | 0
2025-02-20 07:00 | 0 | 0 | 0 | 0 | 0
2025-02-20 08:00 | 0 | 0 | 0 | 0 | 0
2025-02-20 09:00 | 0 | 0 | 0 | 0 | 0
2025-02-20 10:00 | 0 | 0 | 0 | 0 | 0
2025-02-20 11:00 | 0 | 0 | 0 | 0 | 0
2025-02-20 12:00 | 0 | 0 | 0 | 0 | 0
2025-02-20 13:00 | 0 | 0 | 0 | 0 | 0
2025-02-20 14:00 | 0 | 0 | 0 | 0 | 0
2025-02-20 15:00 | 0 | 0 | 0 | 0 | 0
2025-02-20 16:00 | 0 | 0 | 0 | 0 | 0
2025-02-20 17:00 | 0 | 0 | 0 | 0 | 0
2025-02-20 18:00 | 0 | 0 | 0 | 0 | 0
2025-02-20 19:00 | 0 | 0 | 0 | 0 | 0
2025-02-20 20:00 | 0 | 0 | 0 | 0 | 0
2025-02-20 21:00 | 0 | 0 | 0 | 0 | 0
2025-02-20 22:00 | 0 | 0 | 0 | 0 | 0
2025-02-20 23:00 | 0 | 0 | 0 | 0 | 0
2025-02-21 | 0 | 0 | 0 | 0 | 0
2025-02-21 01:00 | 0 | 0 | 0 | 0 | 0
2025-02-21 02:00 | 0.215 | 0 | 0.019392 | 0.19561 | -0.019392
2025-02-21 03:00 | 0.215 | 1.7 | 1.7144 | -1.4994 | -0.01436
2025-02-21 04:00 | 1.7 | 1.7 | 1.735 | -0.03501 | -0.03501
2025-02-21 05:00 | 1.7 | 1.7 | 1.7369 | -0.03687 | -0.03687
2025-02-21 06:00 | 1.7 | 1.7 | 1.732 | -0.032 | -0.032
2025-02-21 07:00 | 2.1 | 2.1 | 1.734 | 0.36605 | 0.36605
2025-02-21 08:00 | 1.7 | 2.1 | 1.7357 | -0.03571 | 0.36429
2025-02-21 09:00 | 0 | 2.1 | 0.022276 | -0.022276 | 2.0777
2025-02-21 10:00 | 0 | 2.1 | 0 | 0 | 2.1
2025-02-21 11:00 | 0 | 0 | 0 | 0 | 0
2025-02-21 12:00 | 0 | 0 | 0 | 0 | 0
2025-02-21 13:00 | 0 | 0 | 0 | 0 | 0
2025-02-21 14:00 | 0 | 0 | 0 | 0 | 0
2025-02-21 15:00 | 0 | 1.8 | 0 | 0 | 1.8
2025-02-21 16:00 | 0 | 1.8 | 0 | 0 | 1.8
2025-02-21 17:00 | 0 | 1.8 | 0 | 0 | 1.8
2025-02-21 18:00 | 0 | 0.6 | 0 | 0 | 0.6
2025-02-21 19:00 | 0 | 0 | 0 | 0 | 0
2025-02-21 20:00 | 0 | 0 | 0 | 0 | 0
2025-02-21 21:00 | 0 | 0 | 0 | 0 | 0
2025-02-21 22:00 | 0 | 0 | 0 | 0 | 0
2025-02-21 23:00 | 0 | 0 | 0 | 0 | 0
2025-02-22 | 0 | 0 | 0 | 0 | 0
2025-02-22 01:00 | 0 | 0 | 0 | 0 | 0
2025-02-22 02:00 | 0 | 0 | 0 | 0 | 0
2025-02-22 03:00 | 0 | 0 | 0 | 0 | 0
2025-02-22 04:00 | 0 | 0 | 0 | 0 | 0
2025-02-22 05:00 | 0 | 0 | 0 | 0 | 0
2025-02-22 06:00 | 0 | 0 | 0 | 0 | 0
2025-02-22 07:00 | 0 | 0 | 0 | 0 | 0
2025-02-22 08:00 | 0 | 0 | 0 | 0 | 0
2025-02-22 09:00 | 0 | 0 | 0.99878 | -0.99878 | -0.99878
2025-02-22 10:00 | 2.1 | 0 | 2.1368 | -0.03683 | -2.1368
2025-02-22 11:00 | 2.1 | 0 | 2.186 | -0.08599 | -2.186
2025-02-22 12:00 | 2.1 | 0 | 2.1898 | -0.08979 | -2.1898
2025-02-22 13:00 | 2.1 | 0 | 2.1911 | -0.0911 | -2.1911
2025-02-22 14:00 | 2.1 | 0 | 2.1911 | -0.09114 | -2.1911
2025-02-22 15:00 | 2.1 | 1.4 | 2.1896 | -0.08957 | -0.78957
2025-02-22 16:00 | 2.1 | 1.6 | 2.1906 | -0.09062 | -0.59062
2025-02-22 17:00 | 2.1 | 1.6 | 2.1888 | -0.08883 | -0.58883
2025-02-22 18:00 | 2.1 | 1.4 | 2.1889 | -0.08893 | -0.78893
2025-02-22 19:00 | 2.1 | 0 | 2.1875 | -0.08749 | -2.1875
2025-02-22 20:00 | 2.1 | 0 | 2.1898 | -0.08982 | -2.1898
2025-02-22 21:00 | 2.1 | 0 | 2.189 | -0.08896 | -2.189
2025-02-22 22:00 | 2.1 | 0 | 2.1886 | -0.08861 | -2.1886
2025-02-22 23:00 | 2.1 | 2.1 | 2.1893 | -0.08928 | -0.08928
2025-02-23 | 2.1 | 2.1 | 2.1892 | -0.08922 | -0.08922
2025-02-23 01:00 | 2.1 | 2.1 | 2.1888 | -0.0888 | -0.0888
2025-02-23 02:00 | 2.1 | 2.1 | 2.1879 | -0.08793 | -0.08793
2025-02-23 03:00 | 2.1 | 2.1 | 2.1897 | -0.0897 | -0.0897
2025-02-23 04:00 | 2.1 | 2.1 | 2.1901 | -0.09008 | -0.09008
2025-02-23 05:00 | 2.1 | 2.1 | 2.1895 | -0.0895 | -0.0895
2025-02-23 06:00 | 2.1 | 2.1 | 2.19 | -0.09002 | -0.09002
2025-02-23 07:00 | 2.1 | 2.1 | 2.1902 | -0.09017 | -0.09017
2025-02-23 08:00 | 2.1 | 2.1 | 2.1899 | -0.08989 | -0.08989
2025-02-23 09:00 | 2.1 | 2.1 | 2.1904 | -0.09043 | -0.09043
2025-02-23 10:00 | 2.1 | 2.1 | 2.1887 | -0.08871 | -0.08871
2025-02-23 11:00 | 2.1 | 2.1 | 2.189 | -0.08896 | -0.08896
2025-02-23 12:00 | 2.1 | 2.1 | 2.1896 | -0.08957 | -0.08957
2025-02-23 13:00 | 2.1 | 2.1 | 2.1893 | -0.08934 | -0.08934
2025-02-23 14:00 | 2.1 | 2.1 | 2.1898 | -0.08982 | -0.08982
2025-02-23 15:00 | 2.1 | 2.1 | 2.1896 | -0.08964 | -0.08964
2025-02-23 16:00 | 2.1 | 2.1 | 2.1912 | -0.0912 | -0.0912
2025-02-23 17:00 | 2.1 | 2.1 | 2.1892 | -0.08918 | -0.08918
2025-02-23 18:00 | 2.1 | 2.1 | 2.189 | -0.08896 | -0.08896
2025-02-23 19:00 | 2.1 | 2.1 | 2.1883 | -0.08829 | -0.08829
2025-02-23 20:00 | 2.1 | 2.1 | 2.188 | -0.08803 | -0.08803
2025-02-23 21:00 | 2.1 | 2.1 | 2.1865 | -0.08646 | -0.08646
2025-02-23 22:00 | 2.1 | 2.1 | 2.1849 | -0.08487 | -0.08487
2025-02-23 23:00 | 2.1 | 2.1 | 2.1868 | -0.08681 | -0.08681
2025-02-24 | 2.1 | 2.1 | 2.1817 | -0.0817 | -0.0817
2025-02-24 01:00 | 2.1 | 2.1 | 2.1854 | -0.08541 | -0.08541
2025-02-24 02:00 | 2.1 | 2.1 | 2.19 | -0.08998 | -0.08998
2025-02-24 03:00 | 2.1 | 2.1 | 2.1915 | -0.09155 | -0.09155
2025-02-24 04:00 | 2.1 | 2.1 | 2.1948 | -0.09479 | -0.09479
2025-02-24 05:00 | 2.1 | 2.1 | 2.1965 | -0.09648 | -0.09648
2025-02-24 06:00 | 2.1 | 2.1 | 2.1882 | -0.08816 | -0.08816
2025-02-24 07:00 | 2.1 | 2.1 | 2.1806 | -0.08061 | -0.08061
2025-02-24 08:00 | 2.1 | 2.1 | 2.1973 | -0.09734 | -0.09734
2025-02-24 09:00 | 2.1 | 2.1 | 2.1906 | -0.09062 | -0.09062
2025-02-24 10:00 | 2.1 | 2.1 | 2.1926 | -0.09255 | -0.09255
2025-02-24 11:00 | 2.1 | 2.1 | 2.1938 | -0.09376 | -0.09376
2025-02-24 12:00 | 2.1 | 2.1 | 2.1921 | -0.09213 | -0.09213
2025-02-24 13:00 | 2.1 | 2.1 | 0.85475 | 1.2452 | 1.2452
2025-02-24 14:00 | 2.1 | 2.1 | 2.0968 | 0.00317 | 0.00317
2025-02-24 15:00 | 2.1 | 2.1 | 2.1985 | -0.09849 | -0.09849
2025-02-24 16:00 | 2.1 | 2.1 | 2.1965 | -0.09645 | -0.09645
2025-02-24 17:00 | 2.1 | 2.1 | 2.1945 | -0.0945 | -0.0945
2025-02-24 18:00 | 2.1 | 2.1 | 2.1938 | -0.09379 | -0.09379
2025-02-24 19:00 | 2.1 | 2.1 | 2.1935 | -0.0935 | -0.0935
2025-02-24 20:00 | 2.1 | 2.1 | 2.1936 | -0.09357 | -0.09357
2025-02-24 21:00 | 2.1 | 2.1 | 2.192 | -0.09203 | -0.09203
2025-02-24 22:00 | 2.1 | 2.1 | 2.1892 | -0.08916 | -0.08916
2025-02-24 23:00 | 2.1 | 2.1 | 2.192 | -0.09203 | -0.09203
2025-02-25 | 2.1 | 2.1 | 2.1915 | -0.09149 | -0.09149
2025-02-25 01:00 | 2.1 | 2.1 | 2.1901 | -0.09014 | -0.09014
2025-02-25 02:00 | 2.1 | 2.1 | 2.1901 | -0.09014 | -0.09014
2025-02-25 03:00 | 2.1 | 2.1 | 2.1887 | -0.08874 | -0.08874
2025-02-25 04:00 | 2.1 | 2.1 | 2.1784 | -0.07837 | -0.07837
2025-02-25 05:00 | 2.1 | 2.1 | 2.1773 | -0.07731 | -0.07731
2025-02-25 06:00 | 2.1 | 2.1 | 2.1773 | -0.07728 | -0.07728
2025-02-25 07:00 | 2.1 | 2.1 | 2.1784 | -0.07837 | -0.07837
2025-02-25 08:00 | 2.1 | 2.1 | 2.1777 | -0.07773 | -0.07773
2025-02-25 09:00 | 2.1 | 2.1 | 2.1768 | -0.07683 | -0.07683
2025-02-25 10:00 | 2.1 | 2.1 | 1.9938 | 0.10618 | 0.10618
2025-02-25 11:00 | 2.1 | 2.1 | 1.666 | 0.43395 | 0.43395
2025-02-25 12:00 | 2.1 | 2.1 | 2.1957 | -0.09572 | -0.09572
2025-02-25 13:00 | 2.1 | 2.1 | 2.1918 | -0.0918 | -0.0918
2025-02-25 14:00 | 2.1 | 2.1 | 2.1808 | -0.08077 | -0.08077
2025-02-25 15:00 | 2.1 | 2.1 | 2.1829 | -0.08285 | -0.08285
2025-02-25 16:00 | 2.1 | 2.1 | 2.1818 | -0.08176 | -0.08176
2025-02-25 17:00 | 2.1 | 2.1 | 2.1789 | -0.07891 | -0.07891
2025-02-25 18:00 | 2.1 | 2.1 | 2.1791 | -0.07911 | -0.07911
2025-02-25 19:00 | 2.1 | 2.1 | 2.1775 | -0.07747 | -0.07747
2025-02-25 20:00 | 2.1 | 2.1 | 2.1791 | -0.07913 | -0.07913
2025-02-25 21:00 | 2.1 | 2.1 | 2.1765 | -0.07648 | -0.07648
2025-02-25 22:00 | 2.1 | 2.1 | 2.178 | -0.07805 | -0.07805
2025-02-25 23:00 | 2.1 | 2.1 | 2.1766 | -0.07661 | -0.07661
2025-02-26 | 2.1 | 2.1 | 2.1772 | -0.07725 | -0.07725
2025-02-26 01:00 | 2.1 | 2.1 | 2.1757 | -0.07571 | -0.07571
2025-02-26 02:00 | 2.1 | 2.1 | 2.1776 | -0.0776 | -0.0776
2025-02-26 03:00 | 2.1 | 2.1 | 2.1769 | -0.07693 | -0.07693
2025-02-26 04:00 | 2.1 | 2.1 | 2.1756 | -0.07558 | -0.07558
2025-02-26 05:00 | 2.1 | 2.1 | 2.1751 | -0.07514 | -0.07514
2025-02-26 06:00 | 2.1 | 2.1 | 2.1771 | -0.07712 | -0.07712
2025-02-26 07:00 | 2.1 | 2.1 | 2.1781 | -0.07814 | -0.07814
2025-02-26 08:00 | 2.1 | 2.1 | 2.1953 | -0.09533 | -0.09533
2025-02-26 09:00 | 2.1 | 2.1 | 2.1956 | -0.09558 | -0.09558
2025-02-26 10:00 | 2.1 | 2.1 | 2.1954 | -0.09536 | -0.09536
2025-02-26 11:00 | 2.1 | 2.1 | 2.1955 | -0.09549 | -0.09549
2025-02-26 12:00 | 2.1 | 2.1 | 2.1947 | -0.09469 | -0.09469
2025-02-26 13:00 | 2.1 | 2.1 | 2.1944 | -0.09437 | -0.09437
2025-02-26 14:00 | 2.1 | 2.1 | 2.1943 | -0.0943 | -0.0943
2025-02-26 15:00 | 2.1 | 2.1 | 2.1933 | -0.09328 | -0.09328
2025-02-26 16:00 | 2.1 | 2.1 | 2.1865 | -0.0865 | -0.0865
2025-02-26 17:00 | 2.1 | 2.1 | 2.1875 | -0.08752 | -0.08752
2025-02-26 18:00 | 2.1 | 2.1 | 2.1869 | -0.08694 | -0.08694
2025-02-26 19:00 | 2.1 | 2.1 | 2.1867 | -0.08669 | -0.08669
2025-02-26 20:00 | 2.1 | 2.1 | 2.1869 | -0.08694 | -0.08694
2025-02-26 21:00 | 2.1 | 2.1 | 2.1868 | -0.08682 | -0.08682
2025-02-26 22:00 | 2.1 | 2.1 | 2.1869 | -0.08694 | -0.08694
2025-02-26 23:00 | 2.1 | 1.4 | 2.1863 | -0.08634 | -0.78634
2025-02-27 | 2.1 | 1.4 | 2.1844 | -0.08442 | -0.78442
2025-02-27 01:00 | 2.1 | 1.4 | 2.1857 | -0.08572 | -0.78572
2025-02-27 02:00 | 2.1 | 1.4 | 2.1865 | -0.0865 | -0.7865
2025-02-27 03:00 | 2.1 | 1.6 | 2.1858 | -0.08576 | -0.58576
2025-02-27 04:00 | 2.1 | 1.6 | 2.1855 | -0.0855 | -0.5855
2025-02-27 05:00 | 2.1 | 1.6 | 2.1849 | -0.08493 | -0.58493
2025-02-27 06:00 | 2.1 | 1.6 | 2.1849 | -0.08493 | -0.58493
2025-02-27 07:00 | 2.1 | 2.1 | 2.185 | -0.08496 | -0.08496
2025-02-27 08:00 | 2.1 | 2.1 | 2.1867 | -0.08672 | -0.08672
2025-02-27 09:00 | 2.1 | 2.1 | 2.1847 | -0.08467 | -0.08467
2025-02-27 10:00 | 2.1 | 2.1 | 2.184 | -0.08403 | -0.08403
2025-02-27 11:00 | 2.1 | 2.1 | 2.1831 | -0.08314 | -0.08314
2025-02-27 12:00 | 2.1 | 1.9 | 2.1843 | -0.08432 | -0.28432
2025-02-27 13:00 | 2.1 | 1.9 | 2.1842 | -0.08416 | -0.28416
2025-02-27 14:00 | 2.1 | 1.8 | 2.1828 | -0.08282 | -0.38282
2025-02-27 15:00 | 2.1 | 2 | 2.1836 | -0.08364 | -0.18364
2025-02-27 16:00 | 2.1 | 2 | 2.1433 | -0.04333 | -0.14333
2025-02-27 17:00 | 2.1 | 2 | 2.141 | -0.04103 | -0.14103
2025-02-27 18:00 | 2.1 | 2 | 2.1674 | -0.06739 | -0.16739
2025-02-27 19:00 | 2.1 | 1.8 | 2.1404 | -0.04035 | -0.34035
2025-02-27 20:00 | 2.1 | 1.8 | 2.1639 | -0.0639 | -0.3639
2025-02-27 21:00 | 2.1 | 0 | 2.1411 | -0.04106 | -2.1411
2025-02-27 22:00 | 2.1 | 0 | 2.1404 | -0.04035 | -2.1404
2025-02-27 23:00 | 2.1 | 2.1 | 2.1399 | -0.03994 | -0.03994
2025-02-28 | 2.1 | 2.1 | 2.1577 | -0.057692 | -0.057692
2025-02-28 01:00 | 2.1 | 2.1 | 2.1456 | -0.04563 | -0.04563
2025-02-28 02:00 | 2.1 | 2.1 | 2.1428 | -0.04278 | -0.04278
2025-02-28 03:00 | 2.1 | 2.1 | 2.1433 | -0.04333 | -0.04333
2025-02-28 04:00 | 2.1 | 2.1 | 2.1433 | -0.04333 | -0.04333
2025-02-28 05:00 | 2.1 | 2.1 | 2.1435 | -0.04352 | -0.04352
2025-02-28 06:00 | 2.1 | 2.1 | 2.143 | -0.04301 | -0.04301
2025-02-28 07:00 | 2.1 | 2.1 | 2.1427 | -0.04275 | -0.04275
2025-02-28 08:00 | 2.1 | 2.1 | 2.1414 | -0.04144 | -0.04144
2025-02-28 09:00 | 2.1 | 2.1 | 2.1416 | -0.04163 | -0.04163
2025-02-28 10:00 | 2.1 | 2.1 | 2.1411 | -0.04106 | -0.04106
2025-02-28 11:00 | 2.1 | 2.1 | 1.6064 | 0.4936 | 0.4936
2025-02-28 12:00 | 2.1 | 2.1 | 2.1416 | -0.04156 | -0.04156
2025-02-28 13:00 | 2.1 | 2.1 | 2.1407 | -0.04068 | -0.04068
2025-02-28 14:00 | 2.1 | 2.1 | 2.1414 | -0.04137 | -0.04137
2025-02-28 15:00 | 2.1 | 2.1 | 2.1381 | -0.03815 | -0.03815
2025-02-28 16:00 | 2.1 | 2.1 | 2.138 | -0.03801 | -0.03801
2025-02-28 17:00 | 2.1 | 2.1 | 2.1376 | -0.03757 | -0.03757
2025-02-28 18:00 | 2.1 | 2.1 | 2.1394 | -0.03942 | -0.03942
2025-02-28 19:00 | 2.1 | 2.1 | 2.1406 | -0.04064 | -0.04064
2025-02-28 20:00 | 2.1 | 2.1 | 2.1398 | -0.03981 | -0.03981
2025-02-28 21:00 | 2.1 | 2.1 | 2.1421 | -0.04208 | -0.04208
2025-02-28 22:00 | 2.1 | 2.1 | 2.1416 | -0.04163 | -0.04163

## Hendelser
Sammenhengende tilstandshendelser
UnitState | Fra (UTC) | Til (UTC) | Timer | MWh sum | Plan sum | Cause
ReserveShutdown | 2025-01-31 23:00 | 2025-02-01 06:00 | 8 | 0 | 0 | M1-MarketDriven
ForcedDerating | 2025-02-01 07:00 | 2025-02-01 07:00 | 1 | 1.1284 | 2 | D1-ForcedDerating
InService | 2025-02-01 08:00 | 2025-02-01 23:00 | 16 | 26.5775 | 25.5 | 0-Normal
ReserveShutdown | 2025-02-02 | 2025-02-02 04:00 | 5 | 0 | 0 | M1-MarketDriven
ForcedOutage | 2025-02-02 05:00 | 2025-02-02 13:00 | 9 | 0 | 0 | U2-UnexpectedStop
InService | 2025-02-02 14:00 | 2025-02-02 14:00 | 1 | 0.019936 | 0 | 0-Normal
ForcedDerating | 2025-02-02 15:00 | 2025-02-02 17:00 | 3 | 0.6175 | 6.3 | D1-ForcedDerating
ForcedOutage | 2025-02-02 18:00 | 2025-02-02 21:00 | 4 | 0 | 4.2 | U1-UnplannedStop
ReserveShutdown | 2025-02-02 22:00 | 2025-02-02 22:00 | 1 | 0 | 0 | M1-MarketDriven
ForcedOutage | 2025-02-02 23:00 | 2025-02-02 23:00 | 1 | 0 | 0 | U2-UnexpectedStop
ReserveShutdown | 2025-02-03 | 2025-02-03 03:00 | 4 | 0 | 0 | M1-MarketDriven
ForcedOutage | 2025-02-03 04:00 | 2025-02-03 12:00 | 9 | 0 | 6.3 | U2-UnexpectedStop
InService | 2025-02-03 13:00 | 2025-02-03 13:00 | 1 | 0.008 | 0 | 0-Normal
ForcedOutage | 2025-02-03 14:00 | 2025-02-03 21:00 | 8 | 0 | 2.1 | U2-UnexpectedStop
ReserveShutdown | 2025-02-03 22:00 | 2025-02-04 04:00 | 7 | 0 | 0 | M1-MarketDriven
ForcedOutage | 2025-02-04 05:00 | 2025-02-04 09:00 | 5 | 0 | 0 | U2-UnexpectedStop
InService | 2025-02-04 10:00 | 2025-02-07 23:00 | 86 | 179.6086 | 166.757 | 0-Normal
ForcedOutage | 2025-02-08 | 2025-02-08 06:00 | 7 | 0 | 12.137 | U1-UnplannedStop
ReserveShutdown | 2025-02-08 07:00 | 2025-02-08 09:00 | 3 | 0 | 0 | M1-MarketDriven
InService | 2025-02-08 10:00 | 2025-02-09 02:00 | 17 | 20.4606 | 18.346 | 0-Normal
ForcedDerating | 2025-02-09 03:00 | 2025-02-09 03:00 | 1 | 0.015366 | 0.668 | D1-ForcedDerating
ForcedOutage | 2025-02-09 04:00 | 2025-02-09 05:00 | 2 | 0 | 1.317 | U1-UnplannedStop
ForcedDerating | 2025-02-09 06:00 | 2025-02-09 06:00 | 1 | 0.024256 | 0.649 | D1-ForcedDerating
InService | 2025-02-09 07:00 | 2025-02-09 19:00 | 13 | 25.4492 | 24.032 | 0-Normal
ForcedOutage | 2025-02-09 20:00 | 2025-02-09 20:00 | 1 | 0 | 0 | U2-UnexpectedStop
ReserveShutdown | 2025-02-09 21:00 | 2025-02-09 23:00 | 3 | 0 | 0 | M1-MarketDriven
ForcedOutage | 2025-02-10 | 2025-02-10 05:00 | 6 | 0 | 12.412 | U1-UnplannedStop
ForcedDerating | 2025-02-10 06:00 | 2025-02-10 06:00 | 1 | 0.013728 | 1.997 | D1-ForcedDerating
InService | 2025-02-10 07:00 | 2025-02-10 08:00 | 2 | 3.6586 | 0 | 0-Normal
ForcedDerating | 2025-02-10 09:00 | 2025-02-10 10:00 | 2 | 1.2338 | 3.578 | D1-ForcedDerating
InService | 2025-02-10 11:00 | 2025-02-10 11:00 | 1 | 1.3093 | 1.3 | 0-Normal
ForcedDerating | 2025-02-10 12:00 | 2025-02-10 12:00 | 1 | 1.0187 | 1.3 | D1-ForcedDerating
InService | 2025-02-10 13:00 | 2025-02-10 15:00 | 3 | 2.667 | 2.6 | 0-Normal
PlannedOutage | 2025-02-10 16:00 | 2025-02-10 23:00 | 8 | 0 | 0 | P1-ScheduledStop
ForcedOutage | 2025-02-11 | 2025-02-11 06:00 | 7 | 0 | 8.725 | U1-UnplannedStop
PlannedOutage | 2025-02-11 07:00 | 2025-02-12 01:00 | 19 | 0 | 0 | P1-ScheduledStop
InService | 2025-02-12 02:00 | 2025-02-12 09:00 | 8 | 11.5902 | 4.741 | 0-Normal
ForcedDerating | 2025-02-12 10:00 | 2025-02-12 10:00 | 1 | 1.6396 | 1.982 | D1-ForcedDerating
InService | 2025-02-12 11:00 | 2025-02-12 23:00 | 13 | 17.5007 | 16.7 | 0-Normal
ForcedOutage | 2025-02-13 | 2025-02-13 05:00 | 6 | 0 | 0 | U2-UnexpectedStop
InService | 2025-02-13 06:00 | 2025-02-13 09:00 | 4 | 6.4837 | 6.3 | 0-Normal
ForcedDerating | 2025-02-13 10:00 | 2025-02-13 10:00 | 1 | 0.031848 | 2.1 | D1-ForcedDerating
ForcedOutage | 2025-02-13 11:00 | 2025-02-13 13:00 | 3 | 0 | 0 | U2-UnexpectedStop
InService | 2025-02-13 14:00 | 2025-02-13 19:00 | 6 | 6.1743 | 5.9 | 0-Normal
ForcedOutage | 2025-02-13 20:00 | 2025-02-14 05:00 | 10 | 0 | 0 | U2-UnexpectedStop
InService | 2025-02-14 06:00 | 2025-02-14 11:00 | 6 | 8.4871 | 8.3 | 0-Normal
ForcedOutage | 2025-02-14 12:00 | 2025-02-14 13:00 | 2 | 0 | 0 | U2-UnexpectedStop
InService | 2025-02-14 14:00 | 2025-02-14 19:00 | 6 | 5.6129 | 5.2 | 0-Normal
ForcedOutage | 2025-02-14 20:00 | 2025-02-15 15:00 | 20 | 0 | 0 | U2-UnexpectedStop
ForcedDerating | 2025-02-15 16:00 | 2025-02-15 16:00 | 1 | 0.76995 | 1.1 | D1-ForcedDerating
InService | 2025-02-15 17:00 | 2025-02-15 19:00 | 3 | 2.2576 | 2.2 | 0-Normal
ForcedOutage | 2025-02-15 20:00 | 2025-02-16 13:00 | 18 | 0 | 0 | U2-UnexpectedStop
InService | 2025-02-16 14:00 | 2025-02-16 17:00 | 4 | 2.6754 | 2.6 | 0-Normal
ForcedOutage | 2025-02-16 18:00 | 2025-02-17 05:00 | 12 | 0 | 10.117 | U1-UnplannedStop
ForcedDerating | 2025-02-17 06:00 | 2025-02-17 06:00 | 1 | 0.041728 | 1.212 | D1-ForcedDerating
InService | 2025-02-17 07:00 | 2025-02-17 09:00 | 3 | 6.3186 | 2.087 | 0-Normal
ForcedDerating | 2025-02-17 10:00 | 2025-02-17 10:00 | 1 | 0.028934 | 2.083 | D1-ForcedDerating
ForcedOutage | 2025-02-17 11:00 | 2025-02-17 13:00 | 3 | 0 | 5.945 | U1-UnplannedStop
InService | 2025-02-17 14:00 | 2025-02-17 19:00 | 6 | 8.0596 | 7.9 | 0-Normal
ForcedOutage | 2025-02-17 20:00 | 2025-02-18 05:00 | 10 | 0 | 11.646 | U2-UnexpectedStop
ForcedDerating | 2025-02-18 06:00 | 2025-02-18 06:00 | 1 | 0.015296 | 1.874 | D1-ForcedDerating
InService | 2025-02-18 07:00 | 2025-02-18 11:00 | 5 | 7.6732 | 3.747 | 0-Normal
ForcedOutage | 2025-02-18 12:00 | 2025-02-19 04:00 | 17 | 0 | 0 | U2-UnexpectedStop
InService | 2025-02-19 05:00 | 2025-02-19 09:00 | 5 | 3.654 | 3.6 | 0-Normal
PlannedOutage | 2025-02-19 10:00 | 2025-02-21 01:00 | 40 | 0 | 0 | P1-ScheduledStop
ForcedDerating | 2025-02-21 02:00 | 2025-02-21 02:00 | 1 | 0.019392 | 0.215 | D1-ForcedDerating
InService | 2025-02-21 03:00 | 2025-02-21 06:00 | 4 | 6.9182 | 5.315 | 0-Normal
ForcedDerating | 2025-02-21 07:00 | 2025-02-21 07:00 | 1 | 1.734 | 2.1 | D1-ForcedDerating
InService | 2025-02-21 08:00 | 2025-02-21 09:00 | 2 | 1.758 | 1.7 | 0-Normal
ReserveShutdown | 2025-02-21 10:00 | 2025-02-21 14:00 | 5 | 0 | 0 | M1-MarketDriven
ForcedOutage | 2025-02-21 15:00 | 2025-02-21 17:00 | 3 | 0 | 0 | U2-UnexpectedStop
ReserveShutdown | 2025-02-21 18:00 | 2025-02-22 08:00 | 15 | 0 | 0 | M1-MarketDriven
InService | 2025-02-22 09:00 | 2025-02-24 12:00 | 52 | 112.6064 | 107.1 | 0-Normal
ForcedDerating | 2025-02-24 13:00 | 2025-02-24 13:00 | 1 | 0.85475 | 2.1 | D1-ForcedDerating
InService | 2025-02-24 14:00 | 2025-02-25 10:00 | 21 | 45.6606 | 44.1 | 0-Normal
ForcedDerating | 2025-02-25 11:00 | 2025-02-25 11:00 | 1 | 1.666 | 2.1 | D1-ForcedDerating
InService | 2025-02-25 12:00 | 2025-02-28 10:00 | 71 | 154.365 | 149.1 | 0-Normal
ForcedDerating | 2025-02-28 11:00 | 2025-02-28 11:00 | 1 | 1.6064 | 2.1 | D1-ForcedDerating
InService | 2025-02-28 12:00 | 2025-02-28 22:00 | 11 | 23.5409 | 23.1 | 0-Normal

## Datakvalitet
Datakvalitetsrapport
Anlegg | Drivdal
Timer forventet | 672
Timer mottatt | 672
Timer akseptert (Good) | 672
Timer flagget | 0
Timer avvist | 0
Per-kolonne statistikk
Kolonne | Null | Non-null | Min | Max | Sum
mwh_elhub | 0 | 672 | 0 | 2.1985 | 703.5547
mwh_esett | 0 | 672 | 0 | 2.1985 | 703.5547
spotbud_mwh | 0 | 672 | 0 | 2.2 | 732.2
spotpris_nok_mwh | 0 | 672 | 313.45 | 2901.03 | 674360.57
spotomsetning_nok | 0 | 672 | 0 | 6092.16 | 754698.55
ubalanse_mwh | 0 | 672 | -2.193 | 2.2 | 28.6453
rk_pris_nok_mwh | 0 | 672 | 172.9496 | 2425.2613 | 584272.2503
rk_kjop_nok | 0 | 672 | -5106.4211 | 0 | -114048.9941
rk_salg_nok | 0 | 672 | 0 | 2091.3679 | 40514.8999
nord_pool_gebyr_nok | 0 | 672 | -2.8782 | 0 | -658.6613
esett_volumgebyr_nok | 0 | 672 | -6.6873 | 0 | -2128.5466
esett_ubalansegebyr_nok | 0 | 672 | -29.5615 | 0 | -2203.8821
sum_salg_nok | 0 | 672 | -108.2512 | 6093.2734 | 676173.3659
meglerprovisjon_nok | 0 | 672 | -1.0992 | 0 | -351.7773
oppgjor_nok | 0 | 672 | -108.2512 | 6092.2145 | 675821.5885
brutto_omsetning_nok | 0 | 672 | 0 | 6137.31 | 650173.28
produksjonplan_mwh | 0 | 672 | 0 | 2.2 | 748.582
effektavlesninger_mw | 0 | 672 | 0 | 2.201 | 704.52
abs_ubalansevolum_mwh | 0 | 672 | 0 | 2.2 | 164.1597
ubalanse_resultat_nok | 0 | 672 | -613.4987 | 3138.4176 | 30991.0064
Avvik og varsler
Alvorlighet | Kode | Melding | Rader